## DOC
"Anchor Bolt (318-08)" --- Embedment Strength per ACI 318-08 Appendix D
Program Description:
"Anchor Bolt(318-08).xls" is a MS-Excel spreadsheet workbook for the analysis of anchor bolt anchorage per
ACI 318-08, Appendix D. The spreadsheet is designed to find the embedment strength of a determined anchor
bolt or bolts within certain concrete parameters. Tables and figures have been given adjacent to the required
data cells in an attempt to self contain the calculations within the worksheet. The spreadsheet is protected
but with no password required.
Program Environment: |  |  | Microsoft Office Excel 2003
Creation Date: |  |  | May 20th, 2008
Design References: |  |  | 1. ACI 318-08
2. Strength Design of Anchorage to Concrete by Ronald A. Cook
This program is a workbook consisting of four (4) worksheets, described as follows:
Worksheet Name |  |  | Description
Doc |  |  | This documentation sheet
Anchorage |  |  | Embedment Strength per ACI 318-08 Appendix D (ver.1.4)
Tension Reinf. |  |  | Anchor Reinforcement per ACI 318-08 Section D.5.2.9 (ver.1.1)
Shear Reinf. |  |  | Anchor Reinforcement per ACI 318-08 Section D.6.2.9 (ver.1.0)
REVISIONS
Anchorage: REVISION 1.5.2 - Revised cell E113 format to have two decimal places.
Tension Reinf.: REVISION 1.1 - (1/19/2015). Revised minimum embed length to reflect hook length.
Program Assumptions and Limitations:
1. This spreadsheet program is intended to analyze and design the embedment of various anchors.
Shear and tension strength is calculated per Appendix D of ACI 318.
2. This program assumes that the anchor strength is not governed by ductile yielding of the anchored steel
which would cause significant redistribution of anchor forces and that the attachment that distributes the
loads to the anchors is sufficiently stiff.
3. The required strength is calculated from the applicable load combinations in Section 9.2.
4. This spreadsheet, as well as the provisions of Appendix D, do not apply to the design of anchors in hinge
zones of concrete structures under seismic loads.
5. Post-installed anchors shall be verified for suitability for use in concrete demonstrated by the ACI 355.2
prequalification tests when installed for use in regions of moderate or high seismic risk, or for structrures
assigned to intermediate or high seismic performance or design catefories.
6. If a ACI 355.2 product evaluation report is used, this program does not account for alternative factors and needs
to be calculated by user.
7. In TENSION REINF. spreadsheet, the edge distance is not in the program's parameters. User must be mindful
that the maximum distance between the anchor and anchor reinforcement must be less than or equal to 0.5 x hef
AND (ED - bc). The latter is not restricted and must be checked by the user.
8. In TENSION REINF. spreadsheet, if the edge distance is less than 1.5 x hef, containment steel such as stirrups
must be used.
9. This program contains numerous “comment boxes” which contain a wide variety of information including
explanations of input or output items, equations used, data tables, etc. (Note: presence of a “comment box”
is denoted by a “red triangle” in the upper right-hand corner of a cell. Merely move the mouse pointer to the
desired cell to view the contents of that particular "comment box".)
Program Theory and Operation: The top left of the spreadsheet screen allows for input of required
information in lightly yellow highlighted boxes. Information required includes the following:
Anchorage Spreadsheet:
Input:
1. Loads:
a. Nua (Ultimate Factored Tensile Load) in kips
b. Vua (Ultimate Factored Shear Load) in kips
2. f Factor Conditions :
a. Steel Element
b. Reinforcement Surfaces
c. Anchor Type
d. Installment Category (Post-installed Anchor only)
e. Cracking from service loads
f. Anchor location
g. Concrete Type
3. Specific Tension and Shear Strength Variables: Each section contains the necessary input variables and
attempts to be self contained.
Output:
1. Steel strength of anchor in tension: (SEC D.5.1)
| Nsa = | nAse,Vfuta
2. Concrete Breakout strength of anchor in tension: (SEC D.5.2)
| Ncb = | Anc | Yed,NYc,NYcp,NNb |  | Single Anchor
Anco
| Ncbg = | Anc | Yec,NYed,NYc,NYcp,NNb |  | Group of Anchors
Anco
3. Pullout strength of anchor in tension: (SEC D.5.3)
| Npn = | Yc,PNp
| Np = | Abrg8f'c |  | The pullout strength in tension of a single headed stud or bolt
| Np = | 0.9f'cehda |  | The pullout strength in tension of a single hooked bolt
4. Concrete Side-Face Blowout strength of Headed anchor in tension: (SEC D.5.4)
| Nsb = | 160ca1Abrg1/2f'c1/2 |  | Single Anchor
| Nsbg = | (1 + s/6ca1)Nsb |  | Hooked Anchor
5. Steel strength of anchor in shear: (SEC D.6.1)
| Vsa = | nAse,Vfuta |  | For cast-in headed stud anchors
| Vsa = | 0.6nAse,Vfuta |  | For cast-in headed bolt & hooked bolt anchors
| Vsa = | 0.6nAse,Vfuta |  | For post-installed anchors
6. Concrete Breakout strength of anchor in shear: (SEC D.6.2)
| Vcb = | Avc | Yed,VYc,VYh,VVb |  | Single Anchor
Avco
| Vcb = | Av | Yec,V Yed,VYc,VYh,VVb |  | Group of Anchors
Avco
7. Concrete Pryout strength of anchor in shear: (SEC D.6.3)
| Vcp = | kcpNcb |  |  | Single Anchor
| Vcpg = | kcpNcbg |  |  | Group of Anchors
8. Interaction of tensile and shear forces: (SEC D.7)
| if Vua < 0.2fVn |  |  |  | fNn > NUA
| if Nua < 0.2fNn |  |  |  | fVn > VUA
| if Nua > 0.2fNn & Vua > 0.2fVn |  |  |  | NUA | + | VUA | < | 1.2
[5 empty] | ΦNn |  | ΦVn
TENSION REINF. Spreadsheet:
Input:
1. Req'd Anchor Reinf. Strength, N: The required anchor reinforcement strength must be equal or larger than
the anchor bolt steel strength, ΦNsa, if anchor design includes earthquake forces for structures assigned
with Seismic Design Category is C,D,E, or F. (ACI Section D3.3)
2. Number of Vert. Reinf., Nr: Number of vertical steel reinforcement bars to resist vertical forces.
3. Estimated Embedment, hef: User's current embedment design of anchor bolts (w/o tension breakout strength
per ACI 318-08 Section D.5.2)
4. Anchor Reinforcement Size: Size of steel rebar from #3 to #14.
5. Reinforcing Yield Strength, fy: in units of ksi
6. Concrete Comp. Strength, f 'c: in units of ksi
7. Lightweight Concrete: If the concrete is lightweight, then "Yes".
8. Epoxy Coated Bars: If bars are epoxy coated, then "Yes".
9. Ratio: As(required)/As(provided): Per Section 12.2.5, the development length may be shortened if the ratio is less
than one. (N/A for Chapter 21 design)
10. Seismic Design per Chapter 21: If anchors are located in structure assigned to Seismic Design Category C, D,
E, or F. (Sect. D3.3), then "Yes".
11. Center-to-Center Bar Spacing, bs: The minimum center-to-center bar spacing between parallel bars in a layer
MUST BE >= 2*db and >= 1". For walls and slabs, maximum center-to-center bar spacing MUST BE <=
3*wall or slab thickness and <= 18".
12. Clear Cover to Face of Bar, bc: Minimum clear cover per Section 7.7.
13. Bolt-Reinf. Distance, d: The bolt-reinforcement distance should be the less than or equal to the maximum
(edge distance - bc) and 0.5hef.
Output:
1. Required Development Length, Ld:
Ld = ((fy*1000)/(f'c*1000)^(1/2)*yt*ye/(l*20))*db*As/As(prov) (Section 12.2.2)
Ld = Maximum of: 3.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 8*db, or 6" (Section 21.7.5)
2. Required Embedment Length:
hef,min = Ld+bc+0.7*d
hef,prov = per embedment entered (See input #3)
3. Required Anchor Reinforcement Size:
As,min = N/(0.75*fy) (Section D.5.2.9)
As,prov = per size and number entered (See input #2 & 4)
SHEAR REINF. Spreadsheet:
Input:
1. Req'd Anchor Reinf. Strength, V: The required anchor reinforcement strength must be equal or larger than the
anchor bolt steel strength,ΦVsa, if anchor design includes earthquake forces for structures assigned with
Seismic Design Category is C,D,E, or F. (ACI Section D3.3)
2. Anchor Reinforcement Size: Size of steel rebar from #3 to #14.
3. Reinforcing Yield Strength, fy: in units of ksi
4. Concrete Comp. Strength, f 'c: in units of ksi
5. Lightweight Concrete: Enter whether the concrete is lightweight or normal weight concrete.
6. Lightweight Concrete: If the concrete is lightweight, then "Yes".
7. Epoxy Coated Bars: If bars are epoxy coated, then "Yes".
development length, then "Yes" (Section 12.2.4(a))
8. Ratio: As(required)/As(provided): Per Section 12.2.5, the development length may be shortened if the ratio is less
than one. (N/A for Chapter 21 design)
9. Seismic Design per Chapter 21: If anchors are located in structure assigned to Seismic Design Category C, D,
E, or F. (Sect. D3.3), then "Yes".
10. Center-to-Center Bar Spacing, bs: The minimum center-to-center bar spacing between parallel bars in a layer
MUST BE >= 2*db and >= 1". For walls and slabs, maximum center-to-center bar spacing MUST BE <=
3*wall or slab thickness and <= 18".
11. Clear Cover to Face of Bar, bc: Minimum clear cover per Section 7.7.
Output:
1. Required Development Length, Ld:
Ld = ((fy*1000)/(f'c*1000)^(1/2)*yt*ye/(l*20))*db*As/As(prov) (Section 12.2.2)
Ld = Maximum of: 3.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 8*db, or 6" (Section 21.7.5)
2. Required Anchor Reinforcement Size:
As,min = V/(0.75*fy) (Section D.5.2.9)
As,prov = per size and number entered (See input #2 & 4)

## ANCHORAGE
ACI318-08 APPENDIX D - ANCHORING TO CONCRETE | [23 empty] | Version 1.5.2 |  | COMMENTARY & SUPPLEMENTAL CALCULATIONS
[11 empty] | MADE BY | [5 empty] | DATE |  |  |  | Job No. | [5 empty] | Summary
[27 empty] | Failure Type |  | Utilization Ratio
[11 empty] | CKD. BY | [5 empty] | DATE |  |  |  | Sheet No. | [5 empty] | Steel Failure (T) |  | 0.15886
[27 empty] | Concrete Breakout (T) |  | 0.65286
FOR | XYZ Baseplate | [25 empty] | Pullout (T) |  | 0.11294
[27 empty] | Side-face Blowout (T) |  | 0.66517
CONCRETE ANCHOR DESIGN BASED ON ACI318-08 APPENDIX D | [26 empty] | Steel Failure (V) |  | 0.097043
| Basic Design Parameters: (SEC D.3-D.4) | [15 empty] | NOTES & SKETCHES | [9 empty] | Concrete Breakout (V) |  | 0.52311
| Loads: |  |  | (Per Applicable Loads Combinations in Sect. 9.2; load applications that are | [22 empty] | Concrete Pryout (V) |  | 0.17281
|  |  |  | predominantly high cycle fatigue or impact loads are not covered.) | [22 empty] | Stress Ratio |  | 1.1883
|  |  | Nua = | 34 |  |  | k |  |  | Ultimate Factored Tensile Load (kips)
|  |  | Vua = | 18 |  |  | k |  |  | Ultimate Factored Shear Load (kips) | [16 empty] | Anchor Type: | Number Identifier
[27 empty] | Headed Stud | 1
| f Factor Conditions: | [25 empty] | Steel f Factor Selection:
[28 empty] | Tension | Shear | Selection
|  |  |  | Ductile | [5 empty] | Steel Element | [16 empty] | Ductile | 0.75 | 0.65 | 0.75 | 0.65
[27 empty] | Brittle | 0.65 | 0.6
|  |  |  | Yes | [5 empty] | Potential Failure Surfaces crossed by supplementary reinforcement
[10 empty] | proportioned to tie prism into the structural member? | [16 empty] | Concrete f Factor Selection:
|  |  |  | Headed Stud | [5 empty] | Anchor Type |  |  |  | NOTE: Hooks bolts are typically not a good design practice. | [13 empty] | Condition A | Condition B
[27 empty] | Shear Loads | 0.75 | 0.7 | 0.75
|  |  |  | Category 1 | [5 empty] | N/A - Only applicable to Post-installed anchors | [16 empty] | Tension Loads
[27 empty] | Cast-in: | 0.75 | 0.7 | 0.75
Post-installed
|  |  |  | Yes | [5 empty] | Anchor located in a region of concrete member where analysis | [16 empty] | Category 1 | 0.75 | 0.65
[10 empty] | indicates no cracking at service load levels? (YES = No Cracking Anticipated) | [16 empty] | Category 2 | 0.65 | 0.55
|  |  |  | No | [5 empty] | Anchors are located in structure assigned to Seismic Design Category C, D, E, or F. (Sect. D3.3) | [16 empty] | Category 3 | 0.55 | 0.45
[27 empty] | Concrete Type: | Number Identifier
|  |  |  | Normalweight | [5 empty] | Concrete Type | [16 empty] | Normalweight | 1
Steel strength of anchor in tension: (SEC D.5.1)
|  | Nsa = |  | nAsefuta | [5 empty] | Assumes no eccentricity in bolt group loading | [9 empty] | (D-3)
|  |  | n = | 4 | [5 empty] | Number of Anchors in a Group
|  |  | Ase, N = | 1.23 |  |  | in2 |  |  | Effective Cross Sectional Area of Anchor
|  |  | futa = | 58 |  |  | ksi |  |  | Specified Tensile strength of anchor steel | [16 empty] | Values used in design:
|  |  | fy = | 36 |  |  | ksi |  |  | Specified Yield strength of anchor steel | [16 empty] | fut = | 58
|  |  | Nsa = | 285.36 |  |  | k | [13 empty] | f = | 0.75
|  |  | fNs = | 214.02 |  |  | k |  | > |  |  | Nu = | 34 |  | k | [9 empty] | OK
Concrete Breakout strength of anchor in tension: (SEC D.5.2)
|  | Ncb = |  | Anc | Yed,NYc,NYcp,NNb | [6 empty] | Single Anchor |  |  |  |  | (D-4)
Anco
|  | Ncbg = |  | Anc | Yec,NYed,NYc,NYcp,NNb | [6 empty] | Group of Anchors |  |  |  |  | (D-5)
Anco
|  |  | Anc = | 1267.5 |  |  | in2 |  |  | Projected concrete failure area of anchor or group of anchors. See RD.6.2.1(b)
|  |  | hef = | 12 |  |  | in |  |  | Effective anchor embedment depth
|  |  | ca,min = | 11.5 |  |  | in |  |  | The smallest edge distance
|  |  | ca,max = | 200 |  |  | in |  |  | The largest edge distance
|  |  | f'c= | 4000 |  |  | psi
|  |  | e'N = | 0 |  |  | in |  |  | Eccentricity of Normal Force on a group of anchor. See Figure RD.5.2.4
|  |  | Edges = | 1 | [5 empty] | Number of Edges surrounding anchor or group of anchors. See Figure RD.5.2.4 Commentary
|  |  | cac = | 12 |  |  | in |  |  | Critical edge distance required to develop the basic concrete breakout strength of a post
installed anchor in uncracked concrete w/o supplementary reinforcement to control splitting.
|  | Anco = |  | 9hef2 | [6 empty] | Projected area of the failure surface of a single anchor remote from edges for ca,min
of 1.5hef or greater
|  | Yec,N = |  | 1 |  |  |  | < 1 |  |  | Modification factor for eccentrically loaded anchor groups
|  |  |  | ( | 1 + | 2e'N | )
3hef
|  | Yed,N = |  | 1 | [6 empty] | if Cmin > 1.5hef Modification factor for edge effects
|  |  | = | 0.7 + 0.3 cmin | [6 empty] | if Cmin < 1.5hef Modification factor for edge effects
1.5 hef
|  | Yc,N = |  | 1.25 | [6 empty] | for Cast-in anchors in uncracked section
|  | Ycp,N = |  | 1 | [6 empty] | for Post-installed anchors in uncracked section w/o supplemental reinforcement
|  | Nb = |  | kclf'c1/2hef3/2 | [6 empty] | Basic concrete breakout strength
k = 24 for cast-in anchor
|  | Nb = |  | 16lf'c1/2hef5/3 | [6 empty] | Alternative concrete breakout strength for 11in < hef < 25in.
|  |  | Anco = | 1296 |  |  | in | 2 | [12 empty] | f = | 0.75
|  |  | Yec,N = | 1
|  |  | Yed,N = | 0.89167
|  |  | Yc,N = | 1.25
|  |  | Ycp,N = | 1
|  |  | Nb = | 63.7008 |  |  | k | [19 empty] | Note: When an additional plate or washer is added at the head of the anchor, it shall be permitted to calculate the projected area of the failure surface by projecting the failure surface outward 1.5hef from the effective perimeter of the plate or washer. (Section D5.2.8)
|  | Ncb | g = | 69.4385 |  |  | k
|  |  | fNcb = | 52.0789 |  |  | k |  | > |  |  | Nu = | 34 |  | k | [9 empty] | OK
Pullout strength of anchor in tension: (SEC D.5.3)
|  | Npn = |  | Yc,PNp | [8 empty] | NOT ONE | [5 empty] | (D-14) | [7 empty] | Values used in design:
[11 empty] | Bearing area of single headed stud or anchor bolt. See Table 1. | [15 empty] | k = | 24
|  |  | Abrg = | 2.24 |  |  | in2 | [19 empty] | Y1 = | 1
|  |  | eh= | 3 |  |  | in |  |  |  | Distance from the inner surface of the shaft to the outer tip of the bolt. 3da<eh<4.5da | [15 empty] | hef = | 12
|  |  | da= | 1 |  |  | in |  |  |  | Outside diameter of anchor or shaft diameter | [15 empty] | An = | 1267.5
|  | Np = |  | Abrg8f'c | [6 empty] | The pullout strength in tension of a single headed stud or bolt | [11 empty] | (D-15) |  |  |  | Fastener Diameter (in.) | Gross Area of Fastener (in.2) | Effective Area of Threaded Fastener | Bearing Area of Heads, Nuts, and Washers (Ab) (in2)
[30 empty] | Square | Heavy Square | Hex | Heavy Hex | Hardened Washers
|  | Np = |  | 0.9f'cehda | [6 empty] | The pullout strength in tension of a single hooked bolt | [11 empty] | (D-16)
[11 empty] | NOTE: Hooks bolts not preferred due to the oil used in bending hook which neglects friction. | [15 empty] | 0.25 | 0.049 | 0.032 | 0.142 | 0.201 | 0.117 | 0.167 | 0.258
|  |  | Yc,P = | 1.4 | [16 empty] | f = | 0.75 |  |  |  |  | 0.375 | 0.11 | 0.078 | 0.28 | 0.362 | 0.164 | 0.299 | 0.408
|  |  | Np = | 100.352 | [6 empty] | Assume that the force is shared evenly w/ other bolts, if multiple anchors. | [15 empty] | 0.5 | 0.196 | 0.142 | 0.464 | 0.569 | 0.291 | 0.464 | 0.69
|  | fNp | g = | 75.264 |  |  | k |  | > |  |  | Nu = | 8.5 |  | k | [9 empty] | OK |  | 0.625 | 0.307 | 0.226 | 0.693 | 0.822 | 0.454 | 0.671 | 1.046
[27 empty] | 0.75 | 0.442 | 0.334 | 0.824 | 1.121 | 0.654 | 0.911 | 1.252
| Concrete Side-Face Blowout strength of Headed anchor in tension: | [25 empty] | 0.875 | 0.601 | 0.462 | 1.121 | 1.465 | 0.891 | 1.188 | 1.804
|  | Single Anchor: | [20 empty] | (SEC D.5.4) |  |  |  | 1 | 0.785 | 0.606 | 1.465 | 1.855 | 1.163 | 1.501 | 2.356
[27 empty] | 1.125 | 0.994 | 0.763 | 1.854 | 2.291 | 1.472 | 1.851 | 2.982
|  | Nsb = |  | 160ca1Abrg1/2lf'c1/2 | [14 empty] | (D-17) | [7 empty] | 1.25 | 1.227 | 0.969 | 2.288 | 2.773 | 1.817 | 2.237 | 3.682
[27 empty] | 1.375 | 1.485 | 1.16 | 2.769 | 3.3 | 2.199 | 2.659 | 4.454
[27 empty] | 1.5 | 1.767 | 1.41 | 3.295 | 3.873 | 2.617 | 3.117 | 5.301
|  |  | Ca1 = | 4 |  |  | in |  |  |  | Distance from center of anchor shaft to the edge of concrete | [15 empty] | 1.75 | 2.405 | 1.9 | - | - | - | 4.144 | 6.541
|  |  | Ca2 = | 6 |  |  | in |  |  |  | Distance from center of anchor shaft to the edge of concrete in direction orthogonal to C = Ca1 See Commentary Figure 1. | [15 empty] | 2 | 3.142 | 2.5 | - | - | - | 5.316 | 7.903
Table 1 Summary of Dimensional Properties of Fasteners
|  |  | Factor = | 0.625 | [6 empty] | Ca2 < 3*Ca1 | [9 empty] | f = | 0.75
|  |  | Nsb = | 37.8629 |  |  | k | [19 empty] | Ronald Cook, "Strength Design of Anchorage to Concrete," PCA, 1999.
|  |  | fNsb = | 28.3972 |  |  | k |  | < |  |  | Nu = | 34 |  | k | [9 empty] | N/A
|  | Multiple Anchors: | [24 empty] | Values used in design:
|  | Nsbg = |  | (1 + s/6ca1)Nsb | [14 empty] | (D-18) | [7 empty] | Ca2/Ca1 = | 1.5
[27 empty] | Use | 1.5
|  |  | s = | 3 |  |  | in |  |  |  | Spacing of the outer anchors along the edge in the group.
|  |  | Nsbg = | 68.1532 |  |  | k | [13 empty] | f = | 0.75
|  |  | fNsbg = | 51.1149 |  |  | k |  | > |  |  | Nu = | 34 |  | k | [9 empty] | OK
Steel strength of anchor in shear: (SEC D.6.1)
|  | Vsa = |  | nAse,Vfuta | [6 empty] | For cast-in headed stud anchors | [8 empty] | (D-19)
|  | Vsa = |  | 0.6nAse,Vfuta | [6 empty] | For cast-in headed bolt & hooked bolt anchors | [8 empty] | (D-20)
|  | Vsa = |  | 0.6nAse,Vfuta | [6 empty] | For post-installed anchors | [8 empty] | (D-20)
|  |  | Grout? | NO | [6 empty] | Is anchor in builtup grout pad?
|  |  | Ase,V= | 1.23 |  |  | in^2 |  |  |  | Effective cross-sectional area of expansion or undercut anchor sleeve, if sleeve is within shear plane.
|  |  | fut= | 58 |  |  | ksi |  |  |  | Specified tensile strength of anchor sleeve.
|  |  | Vsa = | 285.36 |  |  | k | [13 empty] | f = | 0.65
|  |  | fVsa = | 185.484 |  |  | k |  | > |  |  | Vu = | 18 |  | k | [9 empty] | OK
Concrete Breakout strength of anchor in shear: (SEC D.6.2)
|  | Vcb = |  | Avc | Yed,VYc,VYh,VVb | [6 empty] | Single Anchor |  |  | (D-21)
Avco
|  | Vcbg = |  | Avc | Yec,VYed,VYc,VYh,VVb | [6 empty] | Group of Anchors |  |  | (D-22)
Avco
|  |  | Avc = | 498 |  |  | in2 |  |  | Projected concrete failure area on an anchor or group of anchors. See Figure 4 Commentary
|  |  | Ca1* = | 11.5 |  |  | in |  |  | Distance from center of anchor shaft to the edge of concrete in one direction.See Commentary
|  |  | e'v = | 0 |  |  | in |  |  | Eccentricity of shear force on a group of anchors. See Figure 5 Commentary
|  |  | le = | 12 |  |  | in |  |  | Load bearing length of anchor for shear. See Table 2 Commentary.
|  |  | da = | 1.5 |  |  | in |  |  | Outside diameter of anchor or shaft diameter of headed stud, headed bolt, or hooked bolt.
|  |  | ha = | 12 |  |  | in |  |  | Thickness of member in which an anchor is anchored, parallel to anchor axis.
Enter Case: |  |  |  | Case 2 | [5 empty] | Case 1: No supplementary reinforcement or edge reinforcement smaller than a No. 4 bar. Case 2: Supplementary reinforcement of a No. 4 bar or greater between the anchor and the edge. Case 3: Supplementary reinforcement of a No. 4 bar or greater betwwen the anchor and the edge, and with the supplementary reinforcement enclosed withing stirrups spaced at not more than 4 in.
Ca1* Refers to the case where anchors are located at varying distances from the edge and the anchors are welded to the attachment so as to distribute the force to all the anchors, it shall be permitted to evaluate the strength based on the distance to the farthest row of anchors from the edge. In this case, it shall be permitted to base the value of Ca1 (Ca1*) on the distance from the edge to the exis of farthest anchor row that is selected as critical, and all of the shear shall be assumed to be carried by this critical anchor row alone. FOR THE CASE OF A SINGLE ROW LEAVE CELL BLANK
|  | Vb = |  | 7(le/da)0.2da1/2λf'c1/2Ca11.5 | [6 empty] | See commentary
Continued
|  | Yec,V = |  | 1 |  |  |  | < 1 |  |  | Modification factor for eccentrically loaded anchor groups | [15 empty] | Load bearing length of anchor for shear (l)
|  |  |  | ( | 1 + | 2e'v | ) | [19 empty] | l < 8*da = | 12 | in
[6 empty] | 3c1 | [20 empty] | l = hef = | 12 | in | For anchors with a constant stiffness over the full length of the embedded section. i.e. headed studs or post-installed anchors with one tubular shell over the full length of the embedment depth
|  | Yed,V = |  | 1 | [6 empty] | if Ca2 > 1.5Ca1 Modification factor for edge effects
|  |  | = | 0.7 + 0.3 ca2 | [6 empty] | if Ca2 < 1.5Ca1 Modification factor for edge effects
1.5 ca1
[27 empty] | l = 2*da = | 3 | in | For torque-controlled expansion anchors with a distance sleeve separated from the expansion sleeve
|  | Yc,V = |  | 1.4 | [6 empty] | Anchor in uncracked section
|  |  | Yec,V = | 1 | [16 empty] | f = | 0.75 |  |  |  |  | TABLE 2
|  |  | Yed,V = | 0.85
|  |  | Yc,V = | 1.4 | [22 empty] | See code section D.6.2.3 for alternative calculation of Vb.
|  |  | Yh,V = | 1.199 | [6 empty] | Yh,V = (1.5ca1 / ha) ^ 0.5 (where ha < 1.5ca1)
|  |  | Avco = | 288 |  |  | in2 | [19 empty] | Values used for design
|  |  | Vb = | 18.5963 |  |  | k | [19 empty] | 11.5 | Ca1 = | 8 | in
|  | Vcb | g = | 45.879 |  |  | k | [20 empty] | Yec,V = | 1
|  | fVcb | g = | 34.4093 |  |  | k |  | > |  |  | Vu = | 18 |  | k | [9 empty] | OK |  |  | Yed,V = | 0.85
[28 empty] | Av = | 498
Concrete Pryout strength of anchor in shear: (SEC D.6.3)
| Vcp = |  | kcpNcb |  |  |  |  | Single Anchor |  |  |  |  | (D-30)
| Vcpg = |  | kcpNcbg |  |  |  |  | Group of Anchors |  |  |  |  | (D-31)
| Kcp = |  |  | 1 | [6 empty] | for hef < 2.5
| Kcp = |  |  | 2 | [6 empty] | for hef > 2.5
|  | Ncb | g = | 69.4385 |  |  | k | [13 empty] | f = | 0.75
|  | Vcp | g = | 138.8771 |  |  | k
|  | fVcp | g = | 104.1578 |  |  | k |  | > |  |  | Vua = | 18 |  | k | [9 empty] | OK
[27 empty] | Vua < 0.2fVn |  | NO
Nua < 0.2fNn
[27 empty] | Single |  | NO
[27 empty] | Group |  | NO
Nua>0.2fNn & Vua>0.2fVn
| Interaction of tensile and shear forces: (SEC D.7) | [25 empty] | Single |  | 1.7204 | NG
| if Vua < 0.2fVn | [12 empty] | fNn > NUA | [10 empty] | N/A |  | Group |  | 1.1883 | OK
| if Nua < 0.2fNn | [12 empty] | fVn > VUA | [10 empty] | N/A
| if Nua > 0.2fNn & Vua > 0.2fVn | [12 empty] | NUA | + | VUA |  | < | 1.2
[14 empty] | ΦNn |  | ΦVn | [8 empty] | OK
Note on E13: Tension load, Nua, shall be factored per Section 9.2.1. If anchors are located in Seismic Design Category C-F, Nua must set as one of the following: 1. Steel Capacity Nua = Φ n Ase Futa 2. Attaching Member's Ductile Yielding Force, if less than anchor's limits set in D.3.3.3. 3. Higher Factored force Nua = Nua,Previous x 2.5 Nua = Nua,Previous x 2.0 (if anchoring stud bearing wall). NOTE: If concrete capacity is unable to accomodate anchors, additional anchor reinforcement may be required. See "Tension Reinf." or "Shear Reinf." worksheet, if necessary.
Note on E14: Shear load, Vua, shall be factored per Section 9.2.1. If anchors are located in Seismic Design Category C-F, Vua must set as one of the following: 1. Steel Capacity Vua = Φ n Ase Futa (for cast-in headed stud) Vua = 0.6 Φ n Ase Futa (others) 2. Attaching Member's Ductile Yielding Force, if less than anchor's limits set in D.3.3.3. 3. Higher Factored force Vua = Vua,Previous x 2.5 Vua = Vua,Previous x 2.0 (if anchoring stud bearing wall). NOTE: If concrete capacity is unable to accomodate anchors, additional anchor reinforcement may be required. See "Tension Reinf." or "Shear Reinf." worksheet, if necessary.
Note on E20: Ductile: An element with a tensile test elongation of at least 14 percent and reduction in area of at least 30 percent. (Note: ASTM 307 is ductile.) Brittle: An element with a tensile test elongation of less than 14 percent and reduction in area of less than 30 percent, or both.
Note on E22: Supplemental Reinforcement: Reinforcement that has a configuration and placement similar to anchor reinforcement but is not specifically designed to transfer loads from the anchors into the structural member. Stirrups, as used in shear reinforcement, may fall into this category.
Note on E31: If Input is "Yes", anchor must meet the additional requirements of Section D.3.3.1 through D.3.3.6. D.3.3.1 - The provisions of Appendix D do not apply to the design of anchors in plastic zone of concrete structures under earthquake forces. D.3.3.2 - Post-installed structural anchors shall be qualified for use in cracked concrete and shall have passed the Simulated Seismic Tests accordance with ACI 355.2. Pullout strength, Np, and steel strength of the anchor in shear, Vsa, shall be based on the results of the ACI 355.2 Simulated Seismic Tests. D.3.3.3 - The anchor design strength associated with concrete failure modes shall be taken as 0.75ΦNn and 0.75ΦVn, where Φ is given in D.4.4 or D.4.5, and Nn and Vn are determined in accordance with D.5.2, D.5.3, D.5.4, D.6.2 and D.6.3, assuming the concrete is cracked unless it can be demonstrated that the concrete remains uncracked. (This spreadsheet accounts for factor in ouput.) D.3.3.4 - Anchors shall be designed to be governed by the steel strength of a ductile steel element as determined in accordance with D.5.1 and D.6.1, unless either D.3.3.5 or D.3.3.6 is satisfied. D.3.3.5 - Instead of D.3.3.4, the attachment that the anchor is connected to the structure shall be designed so that the attachment will undergo ductile yielding at a force corresponding to anchor forces no greater than the design strength of anchors specified in D.3.3.3. D.3.3.6 - As an alternative to D.3.3.4 & D.3.3.5, it shall be permited to take the design strength of the anchors as 0.4 times the design strength determined in accordance with D.3.3.3. For the anchors of stud bearing wall, it shall be permitted to take the design of the anchors as 0.5 times the design strength determined in accordance with D.3.3.3.
Note on E41: See Table 1 for effective cross section area.
Note on E42: Typical Anchors' Ultimate Strength (ksi) F1554-36 58 F1554-55 75 F1554-105 125 A307 58
Note on E43: Typical Anchors' Yield Strength (ksi) F1554-36 36 F1554-55 55 F1554-105 105 A307 36
1
2
3
4
5
1
2
3
5
6
7
7
7
8
FIGURE 5
FIGURE 4
9
1
2
3
4
5
1
2
3
5
6
7
7
7
8
FIGURE 5
FIGURE 4
9

## TENSION REINF.
TENSION ANCHOR REINFORCEMENT | [18 empty] | Version 1.1
Per Building Code Requirements for Structural Concrete (ACI 318-08) | [8 empty] | CALCULATIONS:
Design of Anchor Reinforcement in place of Concrete Breakout Strength | [7 empty] | Yes | [10 empty] | SUMMARY OF CHECKS:
Job Name: |  |  |  | Subject: | xyz baseplate | Date: | 2026-07-29 17:31 | No |  | Rebar Size |  | Dia. | [6 empty] | Row No.: | Results: | Ratio:
Job Number: |  |  |  | Originator: |  | Checker: |  |  |  | # | 3 | 0.375 | [6 empty] | REQ'D EMBEDMENT LENGTH
[10 empty] | # | 4 | 0.5 | [6 empty] | 28 | Per Section 12.2 | 0.94
Input Data: | [9 empty] | # | 5 | 0.625 | [6 empty] | ANCHOR REINFORCEMENT STRENGTH
|  | Req'd Anchor Reinf. Strength, N = | 35 | kips | [5 empty] | # | 6 | 0.75 | [6 empty] | 32 | Per Section D.5.2.9 | 0.99
|  | Number of Vert. Reinf., Nr = | 4 | [6 empty] | # | 7 | 0.875
|  | Estimated Embedment, hef = | 14 | in. | [5 empty] | # | 8 | 1
|  | Anchor Reinforcement Size = | 4 | (dia. = 0.5'') | [5 empty] | # | 9 | 1.128
|  | Reinforcing Yield Strength, fy = | 60 | ksi | [5 empty] | # | 10 | 1.27
|  | Concrete Comp. Strength, f 'c = | 4 | ksi | [5 empty] | # | 11 | 1.41
|  | Lightweight Concrete? | No | [6 empty] | # | 14 | 1.693
|  | Epoxy Coated Bars? | No | [6 empty] | # | 18 | 2.257
|  | Ratio: As(required)/As(provided) = | 0.74 | [7 empty] | Select: db = | 0.5 | in.
|  | Seismic Design per Chapter 21? | No
|  | Center-to-Center Bar Spacing, bs = | 12 | in.
|  | Clear Cover to Face of Bar, bc = | 2 | in. | [5 empty] | For Straight Bars in Tension - Low Seismic Risk (Sect. 12.2):
|  | Bolt-Reinf. Distance, d = | 6 | in. | [6 empty] | Location Factor, yt = | 1 | Other Bar
[11 empty] | Coating Factor, ye = | 1
| DESIGN SATISFACTORY | [9 empty] | Top Bar Limit: yt*ye = | 1 | <= 1.7
Results: | [10 empty] | Spacing Factor, ys = | 0.8
[11 empty] | Lightweight Factor, l = | 1
Development Length (Section 12.2 or 21.7.5): | [10 empty] | As/As(prov) = | 0.74
Ld = | 17.5506 | in. | [8 empty] | Ld = | 17.5506 | in.
Ldh = | 7.0203 | in. | [7 empty] | High Seismic Risk - Chapter 21 (Sect. 21.7.5)
[11 empty] | Ld = | 23.7171 | in.
Required Anchor Embedment:
hef,min = | 13.2203 | in. | hef,min = Ldh+bc+0.7*d | [6 empty] | Required Anchor Embedment:
hef,prov = | 14 | in. | [8 empty] | Ld = | 17.5506 | in.
[11 empty] | hef, min = | 13.2203 | in. | hef, min = Ldh + bc + 0.7*d
Anchor Reinforcement Strength(Section D.5.2.9): | [10 empty] | hef, prov = | 14 | in.
As,min = | 0.77778 | in2 | As,min = N/(0.75*fy)
As,prov = | 0.7854 | in2 | [7 empty] | Anchor Reinforcement Strength:
[11 empty] | As, min = | 0.77778 | in2 | As, min = N/(0.75*fy)
[11 empty] | As, prov = | 0.7854 | in2
Note: In situations where the edge distance, from centerline of bolts to edge of concrete, is less than 1.5 times
the embedment depth, it is recommended that containment steel, such as stirrups, be used. | [9 empty] | For Standard Hooks in Tension - Low Seismic Risk:
[11 empty] | Cover Factor = | 1
[11 empty] | Tie Factor = | 1
Comments: | [10 empty] | Coating Factor, ye = | 1
[11 empty] | Lightweight Factor, l = | 1
[11 empty] | As/As(prov) = | 0.74 |  |  | High Seismic Risk - Chapter 21
[11 empty] | Ldh = | 7.0203 | in. |  |  | Ldh = | 7.2976 | in.
Note on B26: Per Chapter 12, the straight development length in tension, 'Ld', is calculated as follows: Ld = ((fy*1000)/(f'c*1000)^(1/2)*yt*ye/(l*20))*db*As/As(prov) (Section 12.2.2) where: db = diameter of reinforcing bar yt = reinforcement location factor. = 1.3 for top bars ye = coating factor. = 1.5 for epoxy coated bars with bs < 6*db or bc < 3*db = 1.2 for all other epoxy-coated bars = 1.0 for uncoated bars Note: yt*ye need not be greated than 1.7 l = lightweight aggregate concrete factor. = 0.75 when lightweight aggregate concrete is used = 1.0 when normal weight concrete is used As/As(prov) = excess reinforcing ratio (required/provided) <= 1.0 Per Chapter 21, the straight development length in tension, 'Ld', is calculated as follows: For bar sizes #3 thru #11 and normal weight concrete Ld = Maximum of: 3.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 8*db, or 6" (Section 21.7.5) where: db = diameter of reinforcing bar ye = coating factor. = 1.5 for epoxy coated bars with bs < 6*db or bc < 3*db = 1.2 for all other epoxy-coated bars = 1.0 for uncoated bars For bar sizes #3 thru #11 and lightweight weight concrete Ldt = Maximum of: 3.25*1.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 10*db, or 7.5"
Note on B27: Per Chapter 12, the tension development length for a standard hook bar, 'Ldh', is calculated as follows: Ldh = 0.02*ye/l*(fy*1000)/((f'c*1000)^(1/2))*db, but not less than the larger of 8*db and 6" where: ye = coating factor. = 1.2 for all epoxy-coated bars = 1.0 for uncoated bars l = lightweight aggregate concrete factor. = 0.75 when lightweight aggregate concrete is used = 1.0 when normal weight concrete is used Note: Ldh may be further modified by the following applicable factors: 1. As(req'd)/As(prov) = Excess Reinforcing Factor <= 1.0 2. For #11 bar and smaller, if sc >= 2.5" (program assumes user meets minimum) and bc > 2" for 90 deg. hook, then Cover Factor = 0.7 3. For #11 bar and smaller, if reinforcing is enclosed with ties spaced along length, 'Ldh', and spaced <= 3*db on center, then Tie Factor = 0.8 Per Chapter 21, the tension development length for a standard hook bar, 'Ldh', is calculated as follows: For bar sizes #3 thru #11 and normal weight concrete Ldh = Maximum of: (fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 8*db, or 6" where: db = diameter of reinforcing bar ye = coating factor. = 1.2 for all epoxy-coated bars = 1.0 for uncoated bars For bar sizes #3 thru #11 and lightweight weight concrete Ldh = Maximum of: 1.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 10*db, or 7.5"
Note on D8: The required anchor reinforcement strength, N, must be equal or larger than the anchor bolt steel strength,ΦNsa, if anchor design includes earthquake forces for structures assigned with Seismic Design Category is C,D,E, or F. (ACI Section D3.3)
Note on D11: The Reinforcing Bar Size to input here must be one of the following: 3, 4, 5, 6, 7, 8, 9, 10, 11, 14, and 18
Note on D16: The required development may be reduced by the ratio [As(req'd)/As(prov)] when excess reinforcement is provided in a flexural member. Note that this reduction does not apply when the full 'fy' development is required for tension splices, for development of positive moment reinforcing at supports, and for development of shrinkage and temperature reinforcing. Note also that this reduction in development length is NOT permitted for reinforcing in structures located in regions of high seismic risk. (Section 12.2.5)
Note on D18: Minimum center-to-center bar spacing between parallel bars in a layer MUST BE >= 2*db and >= 1". For walls and slabs, maximum center-to-center bar spacing MUST BE <= 3*wall or slab thickness and <= 18".
Note on D19: Minimum clear cover for CIP (Nonprestressed) Concrete Cover, in. 1. Concrete cast against and permanently exposed to earth………………....3 2. Concrete exposed to earth or weather: No. 6 to 18 bars..................................2 No. 5 or smaller................................1.5 3. Concrete not exposed to weather or in contact with ground: Slabs, walls, and joist: No. 14 & No. 18 bars.........................1.5 No. 11 or smaller.............................0.75 per Section 7.7
Note on D20: The bolt-reinforcement distance, d, should be the less than or equal to the maximum (ED - bc) and 0.5hef.
d
d
bc
bs

## SHEAR REINF.
SHEAR ANCHOR REINFORCEMENT | [13 empty] | Version 1.0
Per Building Code Requirements for Structural Concrete (ACI 318-08) | [7 empty] | CALCULATIONS:
Design of Hairpin Anchor Reinforcement in place of Concrete Breakout Strength | [6 empty] | Yes | [6 empty] | SUMMARY OF CHECKS:
Job Name: |  |  |  | Subject: | Date: | 2026-07-29 17:31 | No |  | Rebar Size |  | Dia. |  |  | Row No.: | Results: | Ratio:
Job Number: |  |  |  | Originator: | Checker: |  |  |  | # | 3 | 0.375 |  |  | ANCHOR REINFORCEMENT STRENGTH
[9 empty] | # | 4 | 0.5 |  |  | 28 | Per Section D.6.2.9 | 0.96
Input Data: | [8 empty] | # | 5 | 0.625
|  | Req'd Anchor Reinf. Strength, V = | 9.5 | kips |  |  |  |  | # | 6 | 0.75
|  | Anchor Reinforcement Size = | 3 | (dia. = 0.375'') |  |  |  |  | # | 7 | 0.875
|  | Reinforcing Yield Strength, fy = | 60 | ksi |  |  |  |  | # | 8 | 1
|  | Concrete Comp. Strength, f 'c = | 4 | ksi |  |  |  |  | # | 9 | 1.128
|  | Lightweight Concrete? | No | [5 empty] | # | 10 | 1.27
|  | Epoxy Coated Bars? | No | [5 empty] | # | 11 | 1.41
|  | Top Bar? | Yes | [5 empty] | # | 14 | 1.693
|  | Ratio: As(required)/As(provided) = | 0.8 | [5 empty] | # | 18 | 2.257
|  | Seismic Design per Chapter 21? | No | [6 empty] | Select: db = | 0.375 | in.
|  | Center-to-Center Bar Spacing, bs = | 12 | in.
|  | Clear Cover to Face of Bar, bc = | 2 | in.
For Straight Bars in Tension - Low Seismic Risk (Sect. 12.2):
| DESIGN SATISFACTORY | [8 empty] | Location Factor, yt = | 1.3
[10 empty] | Coating Factor, ye = | 1
Results: | [9 empty] | Top Bar Limit: yt*ye = | 1.3 | <= 1.7
[10 empty] | Spacing Factor, ys = | 0.8
Development Length (Section 12.2 or 21.7.5): | [9 empty] | Lightweight Factor, l = | 1
Ld = | 18.4993 | in. | [7 empty] | As/As(prov) = | 0.8
[10 empty] | Ld = | 18.4993 | in.
Anchor Reinforcement Strength(Section D.6.2.9): | [8 empty] | High Seismic Risk - Chapter 21 (Sect. 21.7.5)
As,min = | 0.21111 | in2 | As,min = V/(0.75*fy) | [6 empty] | Ld = | 19.5 | in.
As,prov = | 0.22089 | in2 | [6 empty] | Anchor Reinforcement Strength:
[10 empty] | As, min = | 0.21111 | in2 | As, min = V/(0.75*fy)
[10 empty] | As, prov = | 0.22089 | in2
Comments:
Note on B25: Per Chapter 12, the straight development length in tension, 'Ld', is calculated as follows: Ld = ((fy*1000)/(f'c*1000)^(1/2)*yt*ye/(l*20))*db*As/As(prov) (Section 12.2.2) where: db = diameter of reinforcing bar yt = reinforcement location factor. = 1.3 for top bars = 1.0 for other ye = coating factor. = 1.5 for epoxy coated bars with bs < 6*db or bc < 3*db = 1.2 for all other epoxy-coated bars = 1.0 for uncoated bars Note: yt*ye need not be greated than 1.7 l = lightweight aggregate concrete factor. = 0.75 when lightweight aggregate concrete is used = 1.0 when normal weight concrete is used As/As(prov) = excess reinforcing ratio (required/provided) <= 1.0 Per Chapter 21, the straight development length in tension, 'Ld', is calculated as follows: For bar sizes #3 thru #11 and normal weight concrete Ld = Maximum of: 3.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 8*db, or 6" (Section 21.7.5) where: db = diameter of reinforcing bar ye = coating factor. = 1.5 for epoxy coated bars with bs < 6*db or bc < 3*db = 1.2 for all other epoxy-coated bars = 1.0 for uncoated bars For bar sizes #3 thru #11 and lightweight weight concrete Ldt = Maximum of: 3.25*1.25*(fy*1000)*db/(65*(f'c*1000)^(1/2))*ye, 10*db, or 7.5"
Note on D8: The required anchor reinforcement strength, V, must be equal or larger than the anchor bolt steel strength,ΦVsa, if anchor design includes earthquake forces for structures assigned with Seismic Design Category is C,D,E, or F. (ACI Section D3.3)
Note on D9: The Reinforcing Bar Size to input here must be one of the following: 3, 4, 5, 6, 7, 8, 9, 10, 11, 14, and 18
Note on D14: If horizontal reinforcement is placed such that more than 12" of fresh concrete is cast below the development length, then "Yes" Section 12.2.4(a)
Note on D15: The required development may be reduced by the ratio [As(req'd)/As(prov)] when excess reinforcement is provided in a flexural member. Note that this reduction does not apply when the full 'fy' development is required for tension splices, for development of positive moment reinforcing at supports, and for development of shrinkage and temperature reinforcing. Note also that this reduction in development length is NOT permitted for reinforcing in structures located in regions of high seismic risk. (Section 12.2.5)
Note on D17: Minimum center-to-center bar spacing between parallel bars in a layer MUST BE >= 2*db and >= 1". For walls and slabs, maximum center-to-center bar spacing MUST BE <= 3*wall or slab thickness and <= 18".
Note on D18: Minimum clear cover for CIP (Nonprestressed) Concrete Cover, in. 1. Concrete cast against and permanently exposed to earth………………....3 2. Concrete exposed to earth or weather: No. 6 to 18 bars..................................2 No. 5 or smaller................................1.5 3. Concrete not exposed to weather or in contact with ground: Slabs, walls, and joist: No. 14 & No. 18 bars.........................1.5 No. 11 or smaller.............................0.75 per Section 7.7