## DOC
"ROOF DECK" --- Axial, Bending and Shear Capacity of Roof Deck
Program Description:
"ROOF DECK" is a spreadsheet program written in MS-Excel for the purpose of analysis of 1.5 inch
Type 'B' (wide rib) roof deck (using Vulcraft type deck).
Program Environment: | Microsoft Office Excel 2003
Creation Date: | 2010-12-21
Design References: | 1. AISI STANDARD, 2001 Edition. American Iron and Steel Institute.
2. "Steel Roof & Floor Deck"; Vulcraft; 2008 Edition
This program is a workbook consisting of three (3) worksheets, described as follows:
Worksheet Name | Description
Doc | This documentation sheet
DECK | Design of 1 1/2" Type 'B' (wide rib) Roof Deck
AXIALDECK | Axial Capacity of 1 1/2" Type 'B' (wide rib) Roof Deck
Revision 1.1 - 5/10/2010 - Corrected LL deflection formula error in "DECK" worksheet.
Program Assumptions and Limitations:
1. All deck properties are from Vulcraft technical documents.
2. In the "AXIALDECK" worksheet, Roof live loads and wall anchorage lateral loads may be non-concurrent.
3. In the "DECK" worksheet, the number of fasteners are the same at the both end members and interior supports.
4. In the "DECK" worksheet, the number of intermediate sidelap stitch connectors is assumed to be the same
as the number of extreme fasteners.
5. In the "DECK" worksheet, the safety factor for the bare diaphragm shear capacity is 2.35 when mechanically fastened.
If the the lateral loading is seismic or other than wind, the factor of safety shall be modified per Cold-Formed Steel
Structural Members, 2001 Edition w/ 2004 Suppliment.
6. In the "DECK" worksheet, the lateral capacities are based on a 3 span condition. Lesser span conditions result in a
greater shear capacity due to more fasteners, therefore such design is conservative.
7. Where welded sidelaps are shown in the "DECK" worksheet, either use a 5/8" diameter puddle weld or a 3/8" x 1 1/2"
arc seam weld. The Steel Deck Institute (SDI) recommends not welding sidelaps if the deck is 22 Ga or less.
8. Where welds are shown at the supports in the "DECK" worksheet, SDI recommends using welding washers only on
deck thickness less than 0.028" (22Ga). These should be 16Ga with a 3/8" hole in them.
9. The SDI does not recognize button punched sidelaps, with interlocking deck, as a valid sidelap fastener for developing
diaphragm shear strength.
10. These worksheets are limited to three types of thicknesses. Although more are available, the 22, 20 and 18 gauge
thicknesses are most common thickness for roof deck.
11. This program contains numerous “comment boxes” which contain a wide variety of information including
explanations of input or output items, equations used, data tables, etc. (Note: presence of a “comment box”
is denoted by a “red triangle” in the upper right-hand corner of a cell. Merely move the mouse pointer to the
desired cell to view the contents of that particular "comment box".)

## DECK
ROOF DECK | [19 empty] | 1.5B22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)" | [15 empty] | Version 1.1
DESIGN OF 1 1/2" TYPE 'B' (WIDE RIB) ROOF DECK | [10 empty] | CALCULATIONS: | [8 empty] | SUPPORT FASTENERS: 3/4"Φ Puddle Weld w/ 36/7 PATTERN
Using Vulcraft Steel Roof Deck (ICC ER-3415) | [19 empty] | SIDELAP FASTENERS: (7) Welded per span
Job Name: |  |  |  | Subject: |  |  | Date: | 2026-07-30 06:25 | [11 empty] | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF)
Job Number: |  |  |  | Originator: |  |  | Checker: |  | 1.5B22 | [11 empty] | DECK SPAN (FT-IN)
[9 empty] | 1.5B20 | [11 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10
Input Data: | [5 empty] | Member Properties: |  |  | 1.5B18 | [10 empty] | 0 | 585 | 509 | 443 | 391 | 350 | 316 | 288 | 264 | 244 | 226 | 210 | 197 | 186 | 177 | 168
Deck: | [5 empty] | Gage= | 18 | in. | 3/4"Φ Puddle Weld |  |  |  | Matrix Table | [6 empty] | 1 | 734 | 643 | 572 | 514 | 461 | 417 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Deck Size: | 1.5B18 |  |  |  | Thickness,t = | 0.0474 | in. | 5/8"Φ Puddle Weld |  |  |  | Type | Fasteners | v (plf) | K1 | K2 | DB |  | 2 | 866 | 766 | 685 | 619 | 563 | 517 | 473 | 435 | 402 | 374 | 349 | 328 | 310 | 0 | 0
| Deck Length, L = | 6 | ft. |  |  | Wt (psf) = | 2.82 | psf | #12 TEK Screws |  |  |  | 1.5B22 | 1 | 771 | 0.083 | 870 | 129 |  | 3 | 982 | 877 | 790 | 717 | 656 | 603 | 558 | 519 | 481 | 448 | 419 | 384 | 343 | 308 | 278
| # of Span, N = | 3 |  |  |  | In = | 0.295 | in.^4 | Welded |  |  |  |  | 2 | 568 | 0.083 | 870 | 129 |  | 4 | 1083 | 977 | 886 | 808 | 742 | 685 | 635 | 592 | 554 | 494 | 434 | 384 | 343 | 308 | 278
| Deck Horiz. Span, L = | 175 | ft. |  |  | +S | 0.318 | in.^3 | [5 empty] | 3 | 532 | 0.161 | 870 | 129 |  | 5 | 1169 | 1064 | 972 | 892 | 823 | 762 | 709 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  | 1.5B18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
| Deck Vert. Span, B = | 126 | ft. | W |  | -S | 0.327 | in.^3 | 0 |  |  |  |  | 4 | 409 | 0.168 | 870 | 129 |  | 6 | 1244 | 1142 | 1050 | 969 | 898 | 835 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  | SUPPORT FASTENERS: 3/4"Φ Puddle Weld w/ 36/7 PATTERN
[6 empty] | Max Span, Lmax = | 9.1 | ft. | 1 |  |  |  | 1.5B20 | 1 | 1014 | 0.092 | 1056 | 97 |  | 7 | 1308 | 1210 | 1120 | 1039 | 967 | 902 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  | SIDELAP FASTENERS: Welded
[9 empty] | 2 |  |  |  |  | 2 | 776 | 0.092 | 1056 | 97 |  | 8 | 1362 | 1269 | 1182 | 1103 | 1030 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF)
Load: | [8 empty] | 3 |  |  |  |  | 3 | 642 | 0.092 | 1056 | 97 |  | 9 | 1409 | 1321 | 1238 | 1160 | 1088 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  |  | DECK SPAN (FT-IN)
| Dead Load, DL = | 10 | psf | [5 empty] | 4 |  |  |  |  | 4 | 496 | 0.185 | 1398 | 63 |  | 10 | 1450 | 1367 | 1287 | 1212 | 1111 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 |  |  | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10
| Live Load, LL = | 20 | psf | [5 empty] | 5 |  |  |  | 1.5B18 | 1 | 1319 | 0.106 | 1398 | 63 | [18 empty] | 0 | 917 | 797 | 701 | 620 | 555 | 502 | 458 | 421 | 389 | 361 | 337 | 315 | 296 | 279 | 264
| Diaphgram Shear, W = | 1619 | plf | [5 empty] | 6 |  |  |  |  | 2 | 1202 | 0.106 | 1398 | 63 |  | 1.5B20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)" | [16 empty] | 1 | 1148 | 1007 | 894 | 804 | 728 | 660 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 7 |  |  |  |  | 3 | 842 | 0.204 | 1398 | 63 |  | SUPPORT FASTENERS: 3/4"Φ Puddle Weld w/ 36/7 PATTERN | [16 empty] | 2 | 1355 | 1199 | 1072 | 968 | 881 | 808 | 746 | 687 | 636 | 592 | 553 | 519 | 489 | 0 | 0
Deck Attachment: | [8 empty] | 8 |  |  |  |  | 4 | 657 | 0.212 | 1398 | 63 |  | SIDELAP FASTENERS: (7) Welded per span | [16 empty] | 3 | 1536 | 1372 | 1236 | 1121 | 1025 | 943 | 872 | 811 | 757 | 707 | 661 | 621 | 585 | 553 | 524
| Support Fasteners: | [7 empty] | 9 |  |  |  | User Designated deck attachment | [6 empty] | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF) | [15 empty] | 4 | 1693 | 1527 | 1385 | 1264 | 1160 | 1071 | 993 | 925 | 866 | 813 | 766 | 723 | 681 | 644 | 597
| 3/4"Φ Puddle Weld | [7 empty] | 10 |  |  |  | 1.5B22 | 1 | 771 | 0.083 | 870 | 129 |  |  | DECK SPAN (FT-IN) | [15 empty] | 5 | 1829 | 1664 | 1520 | 1395 | 1286 | 1191 | 1108 | 1035 | 970 | 912 | 861 | 815 | 737 | 662 | 597
| Sidelap Fasteners: | [7 empty] | 36/7 |  |  |  | 1.5B20 | 1 | 1014 | 0.092 | 1056 | 97 |  |  | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | 6 | 1946 | 1785 | 1642 | 1515 | 1403 | 1304 | 1217 | 1139 | 1070 | 1008 | 933 | 827 | 737 | 662 | 597
| Welded | [7 empty] | 36/5 |  |  |  | 1.5B18 | 1 | 1319 | 0.106 | 1398 | 63 |  | 0 | 704 | 612 | 535 | 473 | 423 | 382 | 349 | 320 | 295 | 274 | 256 | 239 | 225 | 212 | 202 |  | 7 | 2046 | 1892 | 1751 | 1624 | 1511 | 1409 | 1319 | 1238 | 1165 | 1062 | 933 | 827 | 737 | 662 | 597
| # of Sidelaps: | 7 |  | Summary: | 1.5B18Ga Type B (Wide Rib) Galvanized Deck |  |  |  | 36/4 | [10 empty] | 1 | 882 | 773 | 687 | 618 | 556 | 504 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 2131 | 1985 | 1849 | 1724 | 1610 | 1507 | 1415 | 1331 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
| Weld Pattern: | 36/7 |  |  | weld to supporting steel in a 36/7 pattern |  |  |  | 36/3 |  |  |  | NOTE: | 3/4 & weld | =1 |  |  |  |  | 2 | 1041 | 921 | 824 | 744 | 677 | 621 | 571 | 525 | 486 | 452 | 422 | 396 | 373 | 0 | 0 |  | 9 | 2205 | 2067 | 1936 | 1814 | 1701 | 1598 | 1505 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
[5 empty] | At supports: 3/4"Φ Puddle Weld (36/7 Pattern) | [8 empty] | 5/8 & weld | =2 |  |  |  |  | 3 | 1180 | 1055 | 950 | 862 | 788 | 725 | 671 | 623 | 581 | 541 | 505 | 474 | 447 | 422 | 381 |  | 10 | 2268 | 2138 | 2013 | 1894 | 1784 | 1682 | 1588 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
Analysis: |  |  |  |  | At sidelaps: Welded @ 9 in. O.C. | [8 empty] | 5/8 & #10 | =3 |  |  |  |  | 4 | 1302 | 1174 | 1065 | 972 | 892 | 823 | 764 | 712 | 666 | 625 | 589 | 527 | 470 | 422 | 381
Shear Strength: | [13 empty] | #12 & #10 | =4 |  |  |  |  | 5 | 1406 | 1279 | 1169 | 1073 | 989 | 916 | 852 | 796 | 746 | 676 | 595 | 527 | 470 | 422 | 381
R = | 141662.5 | lbs | R = WL/2 | [16 empty] | 6 | 1495 | 1373 | 1263 | 1165 | 1079 | 1003 | 936 | 876 | 777 | 676 | 595 | 527 | 470 | 422 | 381
S = | 1124.3056 | plf | S = R / B | [16 empty] | 7 | 1572 | 1454 | 1346 | 1249 | 1162 | 1084 | 771 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381
v = | 1319 | plf | Allowable Diaphragm Shear Strength, v |  |  |  |  | OK | [11 empty] | 8 | 1638 | 1526 | 1421 | 1325 | 1238 | 1159 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381
Stiffness: | [19 empty] | 9 | 1694 | 1589 | 1488 | 1394 | 1308 | 1229 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381
K1 = | 0.106 |  | Factor per Vulcraft Table | [16 empty] | 10 | 1743 | 1644 | 1548 | 1457 | 1111 | 1258 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381
K2 = | 1398 |  | Factor per Vulcraft Table
DB = | 63 |  | Factor per Vulcraft Table | [16 empty] | 1.5B18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)"
G' = | 158.1806 | kips/in. | G' = K2 / (3.78 + 0.3*DB / L + 3 K1 L) | [16 empty] | SUPPORT FASTENERS: 3/4"Φ Puddle Weld w/ 36/7 PATTERN
DCL = | 0.31096 | in. | DCL = WL^2 / (8BG') | [16 empty] | SIDELAP FASTENERS: (7) Welded per span
DALLOW = | 8.75 | in. | DALLOW = L (12) / 240 |  |  |  |  | OK | [11 empty] | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF)
Vertical Allowable Loads: | [20 empty] | DECK SPAN (FT-IN)
w = | 32.82 | psf | w = (DL + Wt) + LL | [17 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10
fb = | 4.3359 | ksi | fb = wL^2/(10[-S]) |  |  | (Dependent on N) | [13 empty] | 0 | 917 | 797 | 701 | 620 | 555 | 502 | 458 | 421 | 389 | 361 | 337 | 315 | 296 | 279 | 264
Fb = | 19.8 | ksi | Fb = Fy / 1.67 (Fy = 33ksi) |  |  |  |  | OK |  |  | VULCRAFT SECTION PROPERTIES | [8 empty] | 1 | 1148 | 1007 | 894 | 804 | 728 | 660 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Deflection: | [17 empty] | Max Span, Lmax |  | 2 | 1355 | 1199 | 1072 | 968 | 881 | 808 | 746 | 687 | 636 | 592 | 553 | 519 | 489 | 0 | 0
wLL = | 20 | plf | [8 empty] | GAGE | thk, in | Wt, psf | In, in4/ft | +S, in3/ft | -S, in3/ft | Fy (ksi) | (ft) |  | 3 | 1536 | 1372 | 1236 | 1121 | 1025 | 943 | 872 | 811 | 757 | 707 | 661 | 621 | 585 | 553 | 524
E = | 29000 | ksi | [8 empty] | 22 | 0.0295 | 1.78 | 0.183 | 0.186 | 0.192 | 33 | 6.9167 |  | 4 | 1693 | 1527 | 1385 | 1264 | 1160 | 1071 | 993 | 925 | 866 | 813 | 766 | 723 | 681 | 644 | 597
DLL = | 0.036125 | in. | DLL = | 0.0069 wLL (L)^4/EI | [6 empty] | 20 | 0.0358 | 2.14 | 0.222 | 0.234 | 0.247 | 33 | 7.9167 |  | 5 | 1829 | 1664 | 1520 | 1395 | 1286 | 1191 | 1108 | 1035 | 970 | 912 | 861 | 815 | 737 | 662 | 597
DALLOW = | 0.3 | in. | DALLOW = L (12) / 240 |  |  |  |  | OK |  |  | 18 | 0.0474 | 2.82 | 0.295 | 0.318 | 0.327 | 33 | 9.1 |  | 6 | 1946 | 1785 | 1642 | 1515 | 1403 | 1304 | 1217 | 1139 | 1070 | 1008 | 933 | 827 | 737 | 662 | 597
[20 empty] | 7 | 2046 | 1892 | 1751 | 1624 | 1511 | 1409 | 1319 | 1238 | 1165 | 1062 | 933 | 827 | 737 | 662 | 597
[20 empty] | 8 | 2131 | 1985 | 1849 | 1724 | 1610 | 1507 | 1415 | 1331 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [8 empty] | 9 | 2205 | 2067 | 1936 | 1814 | 1701 | 1598 | 1505 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
[11 empty] | SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/7 PATTERN | [8 empty] | 10 | 2268 | 2138 | 2013 | 1894 | 1784 | 1682 | 1588 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597
SIDELAP FASTENERS: Welded
[11 empty] | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF) | [14 empty] | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | DECK SPAN (FT-IN) | [17 empty] | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[10 empty] | 1 | 0 | 585 | 509 | 443 | 391 | 350 | 316 | 288 | 264 | 244 | 226 | 210 | 197 | 186 | 177 | 168 | 0.486 | 1 | 1 | 288 | 288 | 264
[10 empty] | 2 | 1 | 734 | 643 | 572 | 514 | 461 | 417 | 380 | [8 empty] | 0.287 | 2 | 2 | 380 | 380 | 0
[10 empty] | 3 | 2 | 866 | 766 | 685 | 619 | 563 | 517 | 473 | 435 | 402 | 374 | 349 | 328 | 310 |  |  | 0.204 | 3 | 3 | 473 | 473 | 435
[10 empty] | 4 | 3 | 982 | 877 | 790 | 717 | 656 | 603 | 558 | 519 | 481 | 448 | 419 | 384 | 343 | 308 | 278 | 0.158 | 4 | 4 | 558 | 558 | 519
[10 empty] | 5 | 4 | 1083 | 977 | 886 | 808 | 742 | 685 | 635 | 592 | 554 | 494 | 434 | 384 | 343 | 308 | 278 | 0.129 | 5 | 5 | 635 | 635 | 592
[10 empty] | 6 | 5 | 1169 | 1064 | 972 | 892 | 823 | 762 | 709 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.109 | 6 | 6 | 709 | 709 | 657
[10 empty] | 7 | 6 | 1244 | 1142 | 1050 | 969 | 898 | 835 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.094 | 7 | 7 | 771 | 771 | 657
[10 empty] | 8 | 7 | 1308 | 1210 | 1120 | 1039 | 967 | 902 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.083 | 8 | 8 | 771 | 771 | 657
[10 empty] | 9 | 8 | 1362 | 1269 | 1182 | 1103 | 1030 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.074 | 9 | 9 | 771 | 771 | 657
[10 empty] | 10 | 9 | 1409 | 1321 | 1238 | 1160 | 1088 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.067 | 10 | 10 | 771 | 771 | 657
[10 empty] | 11 | 10 | 1450 | 1367 | 1287 | 1212 | 1111 | 918 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.061 | 11 | 11 | 771 | 771 | 657
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.083
[30 empty] | K2 = | 870
[30 empty] | Db = | 129
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 771 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 518 | 455 | 405 | 361 | 323 | 292 | 266 | 244 | 225 | 208 | 194 | 182 | 172 | 163 | 155 | 0.583 | 1 | 1 | 266 | 266 | 244
[11 empty] | 1 | 1: 641; 2: 572; 3: 514; 4: 466; 5: 426; 6: 392; 7: 358; 9: 383 | 0.319 | 2 | 2 | 358 | 358 | 0
[11 empty] | 2 | 741 | 670 | 609 | 557 | 512 | 473 | 439 | 410 | 449 | 356 | 333 | 312 | 295 |  |  | 0.219 | 3 | 3 | 439 | 439 | 410
[11 empty] | 3 | 821 | 752 | 691 | 637 | 590 | 548 | 511 | 478 | 510 | 423 | 399 | 378 | 343 | 308 | 278 | 0.167 | 4 | 4 | 511 | 511 | 478
[11 empty] | 4 | 884 | 820 | 760 | 707 | 658 | 615 | 576 | 541 | 568 | 481 | 434 | 384 | 343 | 308 | 278 | 0.135 | 5 | 5 | 576 | 576 | 541
[11 empty] | 5 | 934 | 875 | 819 | 767 | 719 | 675 | 635 | 599 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.113 | 6 | 6 | 635 | 635 | 599
[11 empty] | 6 | 974 | 920 | 868 | 818 | 772 | 728 | 688 | 652 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.098 | 7 | 7 | 688 | 688 | 652
[11 empty] | 7 | 1006 | 957 | 909 | 862 | 818 | 775 | 736 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.086 | 8 | 8 | 736 | 736 | 657
[11 empty] | 8 | 1032 | 988 | 944 | 900 | 858 | 817 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.076 | 9 | 9 | 771 | 771 | 657
[11 empty] | 9 | 1054 | 1014 | 973 | 933 | 893 | 854 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.069 | 10 | 10 | 771 | 771 | 657
[11 empty] | 10 | 1071 | 1035 | 998 | 960 | 923 | 886 | 771 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.063 | 11 | 11 | 771 | 771 | 657
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.086
[30 empty] | K2 = | 870
[30 empty] | Db = | 758
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 736 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 396 | 349 | 310 | 273 | 244 | 219 | 199 | 182 | 168 | 155 | 144 | 135 | 127 | 121 | 115 | 0.728 | 1 | 1 | 199 | 199 | 182
[11 empty] | 1 | 1: 514; 2: 461; 3: 416; 4: 379; 5: 347; 6: 320; 7: 292 | 0.358 | 2 | 2 | 292 | 292 | 0
[11 empty] | 2 | 602 | 550 | 504 | 463 | 428 | 397 | 370 | 346 | 324 | 303 | 283 | 266 | 251 |  |  | 0.237 | 3 | 3 | 370 | 370 | 346
[11 empty] | 3 | 666 | 618 | 574 | 534 | 497 | 465 | 436 | 409 | 386 | 364 | 345 | 328 | 312 | 296 | 278 | 0.177 | 4 | 4 | 436 | 436 | 409
[11 empty] | 4 | 714 | 671 | 630 | 592 | 556 | 523 | 493 | 466 | 441 | 418 | 397 | 378 | 343 | 308 | 278 | 0.142 | 5 | 5 | 493 | 493 | 466
[11 empty] | 5 | 749 | 712 | 674 | 639 | 605 | 573 | 543 | 516 | 490 | 467 | 434 | 384 | 343 | 308 | 278 | 0.118 | 6 | 6 | 543 | 543 | 516
[11 empty] | 6 | 776 | 743 | 710 | 677 | 645 | 615 | 586 | 559 | 534 | 494 | 434 | 384 | 343 | 308 | 278 | 0.101 | 7 | 7 | 586 | 586 | 559
[11 empty] | 7 | 796 | 767 | 738 | 708 | 679 | 651 | 623 | 597 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.088 | 8 | 8 | 623 | 623 | 597
[11 empty] | 8 | 812 | 787 | 761 | 734 | 707 | 681 | 655 | 630 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.078 | 9 | 9 | 655 | 655 | 630
[11 empty] | 9 | 824 | 802 | 779 | 755 | 731 | 706 | 682 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.071 | 10 | 10 | 682 | 682 | 657
[11 empty] | 10 | 834 | 815 | 794 | 773 | 750 | 728 | 706 | 657 | 567 | 494 | 434 | 384 | 343 | 308 | 278 | 0.064 | 11 | 11 | 706 | 706 | 657
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.088
[30 empty] | K2 = | 870
[30 empty] | Db = | 1072
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 623 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 331 | 296 | 267 | 242 | 217 | 195 | 177 | 162 | 149 | 137 | 128 | 119 | 113 | 107 | 101 | 0.971 | 1 | 1 | 177 | 177 | 162
[11 empty] | 1 | 1: 417; 2: 383; 3: 353; 4: 326; 5: 302; 6: 281; 7: 262 | 0.408 | 2 | 2 | 262 | 262 | 0
[11 empty] | 2 | 471 | 442 | 414 | 389 | 365 | 343 | 323 | 305 | 288 | 273 | 259 | 247 | 235 |  |  | 0.258 | 3 | 3 | 323 | 323 | 305
[11 empty] | 3 | 506 | 482 | 458 | 435 | 413 | 392 | 372 | 354 | 337 | 321 | 307 | 293 | 280 | 269 | 258 | 0.189 | 4 | 4 | 372 | 372 | 354
[11 empty] | 4 | 529 | 509 | 489 | 469 | 449 | 430 | 412 | 394 | 378 | 362 | 347 | 333 | 320 | 308 | 278 | 0.149 | 5 | 5 | 412 | 412 | 394
[11 empty] | 5 | 544 | 528 | 512 | 494 | 477 | 460 | 443 | 427 | 411 | 396 | 382 | 368 | 343 | 308 | 278 | 0.123 | 6 | 6 | 443 | 443 | 427
[11 empty] | 6 | 555 | 542 | 528 | 513 | 498 | 483 | 468 | 453 | 439 | 424 | 411 | 384 | 343 | 308 | 278 | 0.105 | 7 | 7 | 468 | 468 | 453
[11 empty] | 7 | 563 | 552 | 540 | 528 | 515 | 501 | 488 | 474 | 461 | 448 | 434 | 384 | 343 | 308 | 278 | 0.091 | 8 | 8 | 488 | 488 | 474
[11 empty] | 8 | 569 | 560 | 550 | 539 | 527 | 516 | 504 | 492 | 479 | 467 | 434 | 384 | 343 | 308 | 278 | 0.081 | 9 | 9 | 504 | 504 | 492
[11 empty] | 9 | 573 | 566 | 557 | 548 | 538 | 527 | 517 | 506 | 495 | 484 | 434 | 384 | 343 | 308 | 278 | 0.072 | 10 | 10 | 517 | 517 | 506
[11 empty] | 10 | 577 | 570 | 563 | 555 | 546 | 537 | 527 | 517 | 507 | 494 | 434 | 384 | 343 | 308 | 278 | 0.066 | 11 | 11 | 527 | 527 | 517
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.091
[30 empty] | K2 = | 870
[30 empty] | Db = | 2209
[30 empty] | v = | 488 | plf
1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 484 | 420 | 366 | 323 | 289 | 261 | 238 | 218 | 201 | 187 | 174 | 163 | 154 | 146 | 139 | 0.486 | 1 | 1 | 238 | 238 | 218
[11 empty] | 1 | 1: 630; 2: 554; 3: 493; 4: 443; 5: 400; 6: 362; 7: 330 | 0.287 | 2 | 2 | 330 | 330 | 0
[11 empty] | 2 | 757 | 673 | 604 | 546 | 498 | 457 | 423 | 389 | 360 | 335 | 313 | 283 | 252 |  |  | 0.204 | 3 | 3 | 423 | 423 | 389
[11 empty] | 3 | 865 | 778 | 704 | 641 | 587 | 542 | 502 | 467 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.158 | 4 | 4 | 502 | 502 | 467
[11 empty] | 4 | 956 | 869 | 793 | 727 | 670 | 620 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.129 | 5 | 5 | 568 | 568 | 484
[11 empty] | 5 | 1031 | 947 | 871 | 804 | 745 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.109 | 6 | 6 | 568 | 568 | 484
[11 empty] | 6 | 1093 | 1013 | 940 | 873 | 813 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.094 | 7 | 7 | 568 | 568 | 484
[11 empty] | 7 | 1145 | 1070 | 999 | 934 | 818 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.083 | 8 | 8 | 568 | 568 | 484
[11 empty] | 8 | 1188 | 1118 | 1051 | 988 | 818 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.074 | 9 | 9 | 568 | 568 | 484
[11 empty] | 9 | 1224 | 1160 | 1097 | 1009 | 818 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.067 | 10 | 10 | 568 | 568 | 484
[11 empty] | 10 | 1254 | 1195 | 1136 | 1009 | 818 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.061 | 11 | 11 | 568 | 568 | 484
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.083
[30 empty] | K2 = | 870
[30 empty] | Db = | 129
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 568 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 428 | 376 | 335 | 299 | 267 | 241 | 220 | 201 | 186 | 172 | 160 | 150 | 142 | 134 | 128 | 0.583 | 1 | 1 | 220 | 220 | 201
[11 empty] | 1 | 1: 549; 2: 491; 3: 443; 4: 402; 5: 368; 6: 338; 7: 312 | 0.319 | 2 | 2 | 312 | 312 | 0
[11 empty] | 2 | 642 | 584 | 533 | 489 | 451 | 418 | 388 | 363 | 340 | 320 | 299 | 281 | 252 |  |  | 0.219 | 3 | 3 | 388 | 388 | 363
[11 empty] | 3 | 713 | 658 | 608 | 564 | 524 | 488 | 457 | 428 | 403 | 363 | 319 | 283 | 252 | 226 | 204 | 0.167 | 4 | 4 | 457 | 457 | 428
[11 empty] | 4 | 766 | 716 | 670 | 626 | 586 | 550 | 517 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.135 | 5 | 5 | 517 | 517 | 484
[11 empty] | 5 | 807 | 762 | 719 | 678 | 640 | 604 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.113 | 6 | 6 | 568 | 568 | 484
[11 empty] | 6 | 838 | 798 | 759 | 721 | 685 | 650 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.098 | 7 | 7 | 568 | 568 | 484
[11 empty] | 7 | 862 | 827 | 792 | 757 | 712 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.086 | 8 | 8 | 568 | 568 | 484
[11 empty] | 8 | 881 | 850 | 819 | 787 | 755 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.076 | 9 | 9 | 568 | 568 | 484
[11 empty] | 9 | 896 | 869 | 841 | 812 | 782 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.069 | 10 | 10 | 568 | 568 | 484
[11 empty] | 10 | 908 | 884 | 859 | 832 | 806 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.063 | 11 | 11 | 568 | 568 | 484
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.086
[30 empty] | K2 = | 870
[30 empty] | Db = | 758
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 568 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 328 | 288 | 256 | 226 | 201 | 181 | 165 | 151 | 139 | 128 | 119 | 112 | 105 | 100 | 95 | 0.728 | 1 | 1 | 165 | 165 | 151
[11 empty] | 1 | 1: 442; 2: 398; 3: 361; 4: 329; 5: 302; 6: 278; 7: 257 | 0.358 | 2 | 2 | 257 | 257 | 0
[11 empty] | 2 | 522 | 480 | 442 | 409 | 379 | 353 | 329 | 309 | 290 | 273 | 258 | 242 | 229 |  |  | 0.237 | 3 | 3 | 329 | 329 | 309
[11 empty] | 3 | 577 | 540 | 505 | 472 | 443 | 415 | 391 | 368 | 348 | 330 | 313 | 283 | 252 | 226 | 204 | 0.177 | 4 | 4 | 391 | 391 | 368
[11 empty] | 4 | 615 | 583 | 552 | 522 | 494 | 467 | 443 | 420 | 399 | 363 | 319 | 283 | 252 | 226 | 204 | 0.142 | 5 | 5 | 443 | 443 | 420
[11 empty] | 5 | 642 | 615 | 588 | 561 | 535 | 510 | 486 | 464 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.118 | 6 | 6 | 486 | 486 | 464
[11 empty] | 6 | 662 | 639 | 615 | 591 | 568 | 545 | 522 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.101 | 7 | 7 | 522 | 522 | 484
[11 empty] | 7 | 676 | 657 | 636 | 615 | 594 | 573 | 552 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.088 | 8 | 8 | 552 | 552 | 484
[11 empty] | 8 | 687 | 670 | 653 | 634 | 615 | 596 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.078 | 9 | 9 | 568 | 568 | 484
[11 empty] | 9 | 695 | 681 | 666 | 649 | 633 | 615 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.071 | 10 | 10 | 568 | 568 | 484
[11 empty] | 10 | 702 | 690 | 676 | 662 | 647 | 631 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.064 | 11 | 11 | 568 | 568 | 484
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.088
[30 empty] | K2 = | 870
[30 empty] | Db = | 1072
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 552 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 274 | 245 | 221 | 200 | 179 | 161 | 147 | 134 | 123 | 114 | 105 | 99 | 93 | 88 | 84 | 0.971 | 1 | 1 | 147 | 147 | 134
[11 empty] | 1 | 1: 356; 2: 329; 3: 304; 4: 281; 5: 261; 6: 244; 7: 228 | 0.408 | 2 | 2 | 228 | 228 | 0
[11 empty] | 2 | 403 | 381 | 359 | 339 | 320 | 302 | 285 | 270 | 256 | 243 | 231 | 221 | 211 |  |  | 0.258 | 3 | 3 | 285 | 285 | 270
[11 empty] | 3 | 431 | 413 | 396 | 378 | 361 | 345 | 329 | 314 | 300 | 287 | 275 | 264 | 252 | 226 | 204 | 0.189 | 4 | 4 | 329 | 329 | 314
[11 empty] | 4 | 448 | 434 | 420 | 406 | 391 | 377 | 363 | 349 | 336 | 323 | 311 | 283 | 252 | 226 | 204 | 0.149 | 5 | 5 | 363 | 363 | 349
[11 empty] | 5 | 459 | 448 | 437 | 425 | 413 | 400 | 388 | 375 | 363 | 352 | 319 | 283 | 252 | 226 | 204 | 0.123 | 6 | 6 | 388 | 388 | 375
[11 empty] | 6 | 467 | 458 | 449 | 439 | 428 | 418 | 407 | 396 | 385 | 363 | 319 | 283 | 252 | 226 | 204 | 0.105 | 7 | 7 | 407 | 407 | 396
[11 empty] | 7 | 472 | 465 | 457 | 449 | 440 | 431 | 422 | 412 | 403 | 363 | 319 | 283 | 252 | 226 | 204 | 0.091 | 8 | 8 | 422 | 422 | 412
[11 empty] | 8 | 476 | 470 | 464 | 457 | 449 | 441 | 433 | 425 | 416 | 363 | 319 | 283 | 252 | 226 | 204 | 0.081 | 9 | 9 | 433 | 433 | 425
[11 empty] | 9 | 479 | 474 | 469 | 463 | 456 | 449 | 442 | 435 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.072 | 10 | 10 | 442 | 442 | 435
[11 empty] | 10 | 481 | 477 | 472 | 467 | 462 | 456 | 449 | 443 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.066 | 11 | 11 | 449 | 449 | 443
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.091
[30 empty] | K2 = | 870
[30 empty] | Db = | 2209
[30 empty] | v = | 422 | plf
1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 484; 2: 420; 3: 366; 4: 323; 5: 289 | 0.486 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 557; 2: 487; 3: 432; 4: 383; 5: 343; 6: 310; 7: 283 | 0.377 | 2 | 2 | 283 | 283 | 0
[11 empty] | 2 | 626 | 550 | 489 | 440 | 397 | 359 | 328 | 301 | 278 | 259 | 241 | 227 | 214 | 226 | 204 | 0.308 | 3 | 3 | 328 | 328 | 301
[11 empty] | 3 | 691 | 610 | 545 | 491 | 447 | 408 | 373 | 343 | 317 | 295 | 275 | 258 | 244 | 226 | 204 | 0.261 | 4 | 4 | 373 | 373 | 343
[11 empty] | 4 | 751 | 667 | 598 | 541 | 493 | 452 | 418 | 384 | 355 | 330 | 309 | 283 | 252 | 226 | 204 | 0.226 | 5 | 5 | 418 | 418 | 384
[11 empty] | 5 | 806 | 720 | 648 | 588 | 537 | 494 | 457 | 425 | 394 | 363 | 319 | 283 | 252 | 226 | 204 | 0.199 | 6 | 6 | 457 | 457 | 425
[11 empty] | 6 | 857 | 769 | 696 | 633 | 580 | 534 | 495 | 461 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.178 | 7 | 7 | 495 | 495 | 461
[11 empty] | 7 | 903 | 816 | 741 | 676 | 621 | 574 | 532 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.161 | 8 | 8 | 532 | 532 | 484
[11 empty] | 8 | 946 | 859 | 783 | 717 | 661 | 611 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.147 | 9 | 9 | 568 | 568 | 484
[11 empty] | 9 | 985 | 899 | 823 | 757 | 698 | 648 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.135 | 10 | 10 | 568 | 568 | 484
[11 empty] | 10 | 1021 | 936 | 860 | 794 | 735 | 676 | 568 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.125 | 11 | 11 | 568 | 568 | 484
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.161
[30 empty] | K2 = | 870
[30 empty] | Db = | 129
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 532 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 428; 2: 376; 3: 335; 4: 299; 5: 267 | 0.583 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 490; 2: 435; 3: 389; 4: 352; 5: 321; 6: 290; 7: 265 | 0.433 | 2 | 2 | 265 | 265 | 0
[11 empty] | 2 | 546 | 488 | 440 | 399 | 365 | 336 | 309 | 284 | 263 | 244 | 228 | 214 | 202 |  |  | 0.345 | 3 | 3 | 309 | 309 | 284
[11 empty] | 3 | 594 | 536 | 486 | 443 | 407 | 376 | 348 | 325 | 301 | 280 | 261 | 245 | 232 | 220 | 204 | 0.286 | 4 | 4 | 348 | 348 | 325
[11 empty] | 4 | 637 | 579 | 529 | 485 | 446 | 413 | 384 | 359 | 336 | 316 | 295 | 277 | 252 | 226 | 204 | 0.245 | 5 | 5 | 384 | 384 | 359
[11 empty] | 5 | 675 | 618 | 567 | 523 | 483 | 449 | 419 | 392 | 368 | 346 | 319 | 283 | 252 | 226 | 204 | 0.214 | 6 | 6 | 419 | 419 | 392
[11 empty] | 6 | 707 | 652 | 602 | 558 | 518 | 483 | 451 | 423 | 398 | 363 | 319 | 283 | 252 | 226 | 204 | 0.19 | 7 | 7 | 451 | 451 | 423
[11 empty] | 7 | 736 | 683 | 634 | 590 | 550 | 514 | 482 | 453 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.171 | 8 | 8 | 482 | 482 | 453
[11 empty] | 8 | 761 | 710 | 663 | 619 | 580 | 544 | 511 | 481 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.155 | 9 | 9 | 511 | 511 | 481
[11 empty] | 9 | 782 | 735 | 689 | 647 | 607 | 571 | 538 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.142 | 10 | 10 | 538 | 538 | 484
[11 empty] | 10 | 801 | 756 | 713 | 671 | 633 | 597 | 564 | 484 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.131 | 11 | 11 | 564 | 564 | 484
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.171
[30 empty] | K2 = | 870
[30 empty] | Db = | 758
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 482 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 328; 2: 288; 3: 256; 4: 226; 5: 201 | 0.728 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 388; 2: 345; 3: 310; 4: 281; 5: 255; 6: 230; 7: 210 | 0.509 | 2 | 2 | 210 | 210 | 0
[11 empty] | 2 | 439 | 395 | 358 | 326 | 299 | 276 | 255 | 234 | 216 | 200 | 186 | 175 | 165 |  |  | 0.391 | 3 | 3 | 255 | 255 | 234
[11 empty] | 3 | 482 | 438 | 400 | 367 | 339 | 314 | 292 | 272 | 254 | 236 | 220 | 207 | 195 | 185 | 176 | 0.318 | 4 | 4 | 292 | 292 | 272
[11 empty] | 4 | 518 | 476 | 438 | 405 | 375 | 349 | 325 | 305 | 286 | 270 | 254 | 238 | 225 | 213 | 203 | 0.267 | 5 | 5 | 325 | 325 | 305
[11 empty] | 5 | 548 | 508 | 471 | 438 | 408 | 381 | 357 | 335 | 316 | 298 | 282 | 268 | 252 | 226 | 204 | 0.231 | 6 | 6 | 357 | 357 | 335
[11 empty] | 6 | 573 | 535 | 500 | 467 | 438 | 411 | 386 | 364 | 343 | 325 | 308 | 283 | 252 | 226 | 204 | 0.203 | 7 | 7 | 386 | 386 | 364
[11 empty] | 7 | 594 | 559 | 525 | 494 | 464 | 437 | 413 | 390 | 369 | 350 | 319 | 283 | 252 | 226 | 204 | 0.181 | 8 | 8 | 413 | 413 | 390
[11 empty] | 8 | 611 | 579 | 547 | 517 | 489 | 462 | 437 | 415 | 394 | 363 | 319 | 283 | 252 | 226 | 204 | 0.164 | 9 | 9 | 437 | 437 | 415
[11 empty] | 9 | 626 | 596 | 567 | 538 | 510 | 484 | 460 | 437 | 416 | 363 | 319 | 283 | 252 | 226 | 204 | 0.149 | 10 | 10 | 460 | 460 | 437
[11 empty] | 10 | 639 | 611 | 583 | 556 | 530 | 504 | 481 | 458 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.137 | 11 | 11 | 481 | 481 | 458
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.181
[30 empty] | K2 = | 870
[30 empty] | Db = | 1072
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 413 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 274; 2: 245; 3: 221; 4: 200; 5: 179 | 0.971 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 319; 2: 290; 3: 265; 4: 243; 5: 224; 6: 207; 7: 191 | 0.617 | 2 | 2 | 191 | 191 | 0
[11 empty] | 2 | 354 | 327 | 302 | 279 | 260 | 242 | 226 | 212 | 199 | 185 | 173 | 162 | 153 |  |  | 0.452 | 3 | 3 | 226 | 226 | 212
[11 empty] | 3 | 381 | 356 | 332 | 310 | 290 | 272 | 256 | 241 | 228 | 215 | 204 | 194 | 183 | 173 | 165 | 0.356 | 4 | 4 | 256 | 256 | 241
[11 empty] | 4 | 401 | 378 | 357 | 336 | 317 | 299 | 282 | 267 | 253 | 240 | 229 | 218 | 208 | 199 | 190 | 0.294 | 5 | 5 | 282 | 282 | 267
[11 empty] | 5 | 417 | 397 | 377 | 358 | 339 | 322 | 306 | 290 | 276 | 263 | 251 | 240 | 230 | 220 | 204 | 0.251 | 6 | 6 | 306 | 306 | 290
[11 empty] | 6 | 429 | 411 | 393 | 375 | 358 | 343 | 326 | 311 | 297 | 284 | 272 | 260 | 250 | 226 | 204 | 0.218 | 7 | 7 | 326 | 326 | 311
[11 empty] | 7 | 439 | 423 | 407 | 390 | 374 | 359 | 344 | 329 | 316 | 303 | 290 | 279 | 252 | 226 | 204 | 0.193 | 8 | 8 | 344 | 344 | 329
[11 empty] | 8 | 446 | 432 | 418 | 403 | 388 | 373 | 359 | 345 | 332 | 319 | 307 | 283 | 252 | 226 | 204 | 0.173 | 9 | 9 | 359 | 359 | 345
[11 empty] | 9 | 453 | 440 | 427 | 414 | 400 | 386 | 373 | 360 | 347 | 334 | 319 | 283 | 252 | 226 | 204 | 0.157 | 10 | 10 | 373 | 373 | 360
[11 empty] | 10 | 458 | 447 | 435 | 423 | 410 | 397 | 385 | 372 | 360 | 348 | 319 | 283 | 252 | 226 | 204 | 0.144 | 11 | 11 | 385 | 385 | 372
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.193
[30 empty] | K2 = | 870
[30 empty] | Db = | 2209
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 344 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 283; 2: 246; 3: 214; 4: 189; 5: 169 | 0.549 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 355; 2: 311; 3: 276; 4: 248; 5: 223; 6: 202; 7: 184 | 0.414 | 2 | 2 | 184 | 184 | 0
[11 empty] | 2 | 419 | 371 | 332 | 299 | 273 | 250 | 229 | 210 | 195 | 181 | 169 | 159 | 150 |  |  | 0.333 | 3 | 3 | 229 | 229 | 210
[11 empty] | 3 | 475 | 424 | 382 | 347 | 317 | 292 | 270 | 251 | 233 | 217 | 203 | 190 | 180 | 170 | 162 | 0.278 | 4 | 4 | 270 | 270 | 251
[11 empty] | 4 | 524 | 473 | 429 | 391 | 359 | 332 | 308 | 287 | 268 | 252 | 236 | 222 | 210 | 199 | 189 | 0.239 | 5 | 5 | 308 | 308 | 287
[11 empty] | 5 | 566 | 515 | 471 | 432 | 398 | 369 | 343 | 321 | 301 | 283 | 267 | 253 | 240 | 226 | 204 | 0.209 | 6 | 6 | 343 | 343 | 321
[11 empty] | 6 | 602 | 553 | 508 | 469 | 435 | 404 | 377 | 353 | 332 | 313 | 295 | 280 | 252 | 226 | 204 | 0.186 | 7 | 7 | 377 | 377 | 353
[11 empty] | 7 | 633 | 585 | 542 | 503 | 468 | 437 | 409 | 384 | 361 | 341 | 319 | 283 | 252 | 226 | 204 | 0.168 | 8 | 8 | 409 | 409 | 384
[11 empty] | 8 | 659 | 614 | 572 | 534 | 499 | 467 | 439 | 413 | 389 | 363 | 319 | 283 | 252 | 226 | 204 | 0.152 | 9 | 9 | 439 | 439 | 413
[11 empty] | 9 | 682 | 639 | 599 | 562 | 527 | 495 | 466 | 440 | 416 | 363 | 319 | 283 | 252 | 226 | 204 | 0.14 | 10 | 10 | 466 | 466 | 440
[11 empty] | 10 | 701 | 661 | 623 | 587 | 553 | 521 | 492 | 466 | 417 | 363 | 319 | 283 | 252 | 226 | 204 | 0.129 | 11 | 11 | 492 | 492 | 466
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.168
[30 empty] | K2 = | 870
[30 empty] | Db = | 129
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 409 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 250; 2: 220; 3: 196; 4: 175; 5: 156 | 0.659 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 310; 2: 276; 3: 249; 4: 225; 5: 206; 6: 189; 7: 173 | 0.474 | 2 | 2 | 173 | 173 | 0
[11 empty] | 2 | 358 | 324 | 295 | 269 | 248 | 229 | 213 | 198 | 185 | 172 | 161 | 151 | 143 |  |  | 0.37 | 3 | 3 | 213 | 213 | 198
[11 empty] | 3 | 397 | 364 | 334 | 308 | 285 | 265 | 247 | 231 | 217 | 205 | 193 | 183 | 173 | 164 | 155 | 0.304 | 4 | 4 | 247 | 247 | 231
[11 empty] | 4 | 427 | 396 | 368 | 342 | 319 | 298 | 279 | 262 | 247 | 233 | 221 | 209 | 199 | 190 | 181 | 0.257 | 5 | 5 | 279 | 279 | 262
[11 empty] | 5 | 452 | 423 | 396 | 371 | 348 | 327 | 307 | 290 | 274 | 260 | 246 | 234 | 223 | 213 | 204 | 0.223 | 6 | 6 | 307 | 307 | 290
[11 empty] | 6 | 471 | 445 | 420 | 396 | 373 | 352 | 333 | 315 | 299 | 284 | 270 | 258 | 246 | 226 | 204 | 0.197 | 7 | 7 | 333 | 333 | 315
[11 empty] | 7 | 486 | 463 | 440 | 417 | 396 | 375 | 356 | 339 | 322 | 307 | 293 | 280 | 252 | 226 | 204 | 0.177 | 8 | 8 | 356 | 356 | 339
[11 empty] | 8 | 499 | 478 | 456 | 435 | 415 | 395 | 377 | 359 | 343 | 328 | 314 | 283 | 252 | 226 | 204 | 0.16 | 9 | 9 | 377 | 377 | 359
[11 empty] | 9 | 509 | 490 | 471 | 451 | 432 | 413 | 395 | 378 | 362 | 347 | 319 | 283 | 252 | 226 | 204 | 0.146 | 10 | 10 | 395 | 395 | 378
[11 empty] | 10 | 518 | 500 | 483 | 464 | 446 | 429 | 412 | 395 | 379 | 363 | 319 | 283 | 252 | 226 | 204 | 0.134 | 11 | 11 | 412 | 412 | 395
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.177
[30 empty] | K2 = | 870
[30 empty] | Db = | 758
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 356 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 191; 2: 169; 3: 150; 4: 132; 5: 188 | 0.823 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 248; 2: 223; 3: 201; 4: 183; 5: 168; 6: 155; 7: 141 | 0.554 | 2 | 2 | 141 | 141 | 0
[11 empty] | 2 | 291 | 266 | 244 | 224 | 207 | 192 | 179 | 167 | 157 | 147 | 137 | 129 | 121 |  |  | 0.417 | 3 | 3 | 179 | 179 | 167
[11 empty] | 3 | 322 | 299 | 278 | 258 | 241 | 225 | 211 | 198 | 187 | 176 | 167 | 159 | 151 | 143 | 136 | 0.334 | 4 | 4 | 211 | 211 | 198
[11 empty] | 4 | 345 | 325 | 305 | 286 | 269 | 253 | 239 | 226 | 214 | 202 | 192 | 183 | 175 | 167 | 160 | 0.279 | 5 | 5 | 239 | 239 | 226
[11 empty] | 5 | 362 | 344 | 326 | 309 | 293 | 277 | 263 | 250 | 237 | 226 | 215 | 206 | 197 | 188 | 161 | 0.24 | 6 | 6 | 263 | 263 | 250
[11 empty] | 6 | 375 | 359 | 343 | 328 | 312 | 298 | 284 | 271 | 259 | 247 | 236 | 226 | 217 | 208 | 200 | 0.21 | 7 | 7 | 284 | 284 | 271
[11 empty] | 7 | 385 | 371 | 357 | 343 | 329 | 315 | 302 | 289 | 277 | 266 | 255 | 245 | 235 | 226 | 204 | 0.187 | 8 | 8 | 302 | 302 | 289
[11 empty] | 8 | 392 | 380 | 368 | 355 | 342 | 329 | 317 | 305 | 293 | 282 | 272 | 262 | 252 | 226 | 204 | 0.168 | 9 | 9 | 317 | 317 | 305
[11 empty] | 9 | 398 | 388 | 377 | 365 | 353 | 342 | 330 | 319 | 308 | 297 | 287 | 277 | 252 | 226 | 204 | 0.153 | 10 | 10 | 330 | 330 | 319
[11 empty] | 10 | 403 | 394 | 384 | 373 | 363 | 352 | 341 | 331 | 320 | 310 | 300 | 283 | 252 | 226 | 204 | 0.14 | 11 | 11 | 341 | 341 | 331
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.187
[30 empty] | K2 = | 870
[30 empty] | Db = | 1072
[11 empty] | 1.5B 22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 302 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 160; 2: 143; 3: 129; 4: 117; 5: 105 | 1.098 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 202; 2: 185; 3: 171; 4: 157; 5: 146; 6: 136; 7: 127 | 0.665 | 2 | 2 | 127 | 127 | 0
[11 empty] | 2 | 228 | 214 | 200 | 188 | 176 | 166 | 156 | 147 | 139 | 132 | 126 | 119 | 114 |  |  | 0.477 | 3 | 3 | 156 | 156 | 147
[11 empty] | 3 | 245 | 233 | 222 | 210 | 200 | 190 | 180 | 171 | 163 | 156 | 148 | 142 | 136 | 130 | 125 | 0.372 | 4 | 4 | 180 | 180 | 171
[11 empty] | 4 | 255 | 246 | 236 | 227 | 217 | 208 | 199 | 191 | 183 | 175 | 168 | 161 | 155 | 149 | 143 | 0.305 | 5 | 5 | 199 | 199 | 191
[11 empty] | 5 | 263 | 255 | 247 | 239 | 231 | 222 | 214 | 207 | 199 | 192 | 185 | 178 | 172 | 166 | 160 | 0.258 | 6 | 6 | 214 | 214 | 207
[11 empty] | 6 | 2668 | 262 | 255 | 248 | 241 | 234 | 226 | 219 | 212 | 205 | 199 | 192 | 186 | 180 | 175 | 0.224 | 7 | 7 | 226 | 226 | 219
[11 empty] | 7 | 272 | 267 | 261 | 255 | 249 | 242 | 236 | 229 | 223 | 217 | 210 | 204 | 198 | 192 | 187 | 0.198 | 8 | 8 | 236 | 236 | 229
[11 empty] | 8 | 275 | 270 | 266 | 260 | 255 | 249 | 244 | 238 | 232 | 226 | 220 | 215 | 209 | 204 | 198 | 0.177 | 9 | 9 | 244 | 244 | 238
[11 empty] | 9 | 277 | 273 | 269 | 265 | 260 | 255 | 250 | 245 | 239 | 234 | 229 | 223 | 218 | 213 | 204 | 0.16 | 10 | 10 | 250 | 250 | 245
[11 empty] | 10 | 279 | 275 | 272 | 268 | 264 | 259 | 255 | 250 | 245 | 240 | 236 | 231 | 226 | 221 | 204 | 0.146 | 11 | 11 | 255 | 255 | 250
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.198
[30 empty] | K2 = | 870
[30 empty] | Db = | 2209
[30 empty] | v = | 236 | plf
1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[10 empty] | 1 | 0 | 704 | 612 | 535 | 473 | 423 | 382 | 349 | 320 | 295 | 274 | 256 | 239 | 225 | 212 | 202 | 0.535 | 1 | 1 | 349 | 349 | 320
[10 empty] | 2 | 1 | 1: 882; 2: 773; 3: 687; 4: 618; 5: 556; 6: 504; 7: 460 | 0.317 | 2 | 2 | 460 | 460 | 0
[10 empty] | 3 | 2 | 1041 | 921 | 824 | 744 | 677 | 621 | 571 | 525 | 486 | 452 | 422 | 396 | 373 |  |  | 0.225 | 3 | 3 | 571 | 571 | 525
[10 empty] | 4 | 3 | 1180 | 1055 | 950 | 862 | 788 | 725 | 671 | 623 | 581 | 541 | 505 | 474 | 447 | 422 | 381 | 0.174 | 4 | 4 | 671 | 671 | 623
[10 empty] | 5 | 4 | 1302 | 1174 | 1065 | 972 | 892 | 823 | 764 | 712 | 666 | 625 | 589 | 527 | 470 | 422 | 381 | 0.142 | 5 | 5 | 764 | 764 | 712
[10 empty] | 6 | 5 | 1406 | 1279 | 1169 | 1073 | 989 | 916 | 852 | 796 | 746 | 676 | 595 | 527 | 470 | 422 | 381 | 0.12 | 6 | 6 | 852 | 852 | 796
[10 empty] | 7 | 6 | 1495 | 1373 | 1263 | 1165 | 1079 | 1003 | 936 | 876 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.104 | 7 | 7 | 936 | 936 | 876
[10 empty] | 8 | 7 | 1572 | 1454 | 1346 | 1249 | 1162 | 1084 | 1014 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.092 | 8 | 8 | 1014 | 1014 | 901
[10 empty] | 9 | 8 | 1638 | 1526 | 1421 | 1325 | 1238 | 1159 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.082 | 9 | 9 | 1057 | 1057 | 901
[10 empty] | 10 | 9 | 1694 | 1589 | 1488 | 1394 | 1308 | 1229 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.074 | 10 | 10 | 1057 | 1057 | 901
[10 empty] | 11 | 10 | 1743 | 1644 | 1548 | 1457 | 1372 | 1258 | 1057 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.068 | 11 | 11 | 1057 | 1057 | 901
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.092
[30 empty] | K2 = | 1056
[30 empty] | Db = | 97
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 1014 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 623 | 548 | 488 | 437 | 391 | 353 | 322 | 295 | 273 | 253 | 236 | 220 | 207 | 196 | 186 | 0.642 | 1 | 1 | 322 | 322 | 295
[11 empty] | 1 | 1: 771; 2: 688; 3: 618; 4: 561; 5: 512; 6: 471; 7: 433 | 0.351 | 2 | 2 | 433 | 433 | 0
[11 empty] | 2 | 891 | 806 | 733 | 670 | 616 | 569 | 528 | 492 | 461 | 431 | 402 | 377 | 355 |  |  | 0.242 | 3 | 3 | 528 | 528 | 492
[11 empty] | 3 | 987 | 904 | 831 | 766 | 709 | 658 | 614 | 574 | 539 | 508 | 480 | 455 | 429 | 406 | 381 | 0.184 | 4 | 4 | 614 | 614 | 574
[11 empty] | 4 | 1063 | 985 | 914 | 849 | 791 | 739 | 692 | 650 | 613 | 579 | 548 | 520 | 470 | 422 | 381 | 0.149 | 5 | 5 | 692 | 692 | 650
[11 empty] | 5 | 1123 | 1052 | 984 | 922 | 864 | 811 | 763 | 720 | 680 | 644 | 595 | 527 | 470 | 422 | 381 | 0.125 | 6 | 6 | 763 | 763 | 720
[11 empty] | 6 | 1171 | 1106 | 1043 | 983 | 927 | 875 | 827 | 783 | 743 | 676 | 595 | 527 | 470 | 422 | 381 | 0.108 | 7 | 7 | 827 | 827 | 783
[11 empty] | 7 | 121 | 1151 | 1093 | 1037 | 983 | 932 | 885 | 841 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.094 | 8 | 8 | 885 | 885 | 841
[11 empty] | 8 | 1241 | 1188 | 1135 | 1082 | 1031 | 982 | 936 | 893 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.084 | 9 | 9 | 936 | 936 | 893
[11 empty] | 9 | 1267 | 1219 | 1170 | 1121 | 1073 | 1027 | 982 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.076 | 10 | 10 | 982 | 982 | 901
[11 empty] | 10 | 1288 | 1245 | 1200 | 1155 | 1110 | 1065 | 1023 | 901 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.069 | 11 | 11 | 1023 | 1023 | 901
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.094
[30 empty] | K2 = | 1056
[30 empty] | Db = | 567
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 885 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 477 | 420 | 374 | 331 | 295 | 266 | 242 | 222 | 204 | 189 | 176 | 164 | 154 | 145 | 138 | 0.802 | 1 | 1 | 242 | 242 | 222
[11 empty] | 1 | 1: 618; 2: 554; 3: 501; 4: 456; 5: 417; 6: 384; 7: 353 | 0.394 | 2 | 2 | 353 | 353 | 0
[11 empty] | 2 | 723 | 661 | 606 | 557 | 515 | 477 | 445 | 416 | 390 | 367 | 342 | 321 | 302 |  |  | 0.261 | 3 | 3 | 445 | 445 | 416
[11 empty] | 3 | 801 | 743 | 690 | 642 | 598 | 559 | 524 | 492 | 464 | 438 | 415 | 394 | 375 | 356 | 338 | 0.195 | 4 | 4 | 524 | 524 | 492
[11 empty] | 4 | 858 | 807 | 757 | 711 | 668 | 629 | 593 | 560 | 530 | 503 | 477 | 455 | 433 | 414 | 381 | 0.156 | 5 | 5 | 593 | 593 | 560
[11 empty] | 5 | 901 | 856 | 811 | 768 | 727 | 689 | 653 | 620 | 589 | 561 | 535 | 511 | 470 | 422 | 381 | 0.13 | 6 | 6 | 653 | 653 | 620
[11 empty] | 6 | 933 | 893 | 853 | 814 | 776 | 740 | 705 | 672 | 642 | 613 | 587 | 527 | 470 | 422 | 381 | 0.111 | 7 | 7 | 705 | 705 | 672
[11 empty] | 7 | 957 | 923 | 887 | 852 | 817 | 782 | 749 | 718 | 688 | 660 | 595 | 527 | 470 | 422 | 381 | 0.097 | 8 | 8 | 749 | 749 | 718
[11 empty] | 8 | 976 | 946 | 915 | 883 | 850 | 819 | 788 | 758 | 729 | 676 | 595 | 527 | 470 | 422 | 381 | 0.086 | 9 | 9 | 788 | 788 | 758
[11 empty] | 9 | 991 | 965 | 937 | 908 | 879 | 849 | 820 | 792 | 764 | 676 | 595 | 527 | 470 | 422 | 381 | 0.078 | 10 | 10 | 820 | 820 | 792
[11 empty] | 10 | 1003 | 980 | 955 | 929 | 902 | 875 | 848 | 822 | 777 | 676 | 595 | 527 | 470 | 422 | 381 | 0.071 | 11 | 11 | 848 | 848 | 822
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.097
[30 empty] | K2 = | 1056
[30 empty] | Db = | 802
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 749 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 398 | 356 | 321 | 292 | 264 | 237 | 216 | 197 | 181 | 168 | 156 | 145 | 136 | 129 | 122 | 1.07 | 1 | 1 | 216 | 216 | 197
[11 empty] | 1 | 1: 502; 2: 461; 3: 424; 4: 392; 5: 363; 6: 337; 7: 315 | 0.45 | 2 | 2 | 315 | 315 | 0
[11 empty] | 2 | 567 | 532 | 498 | 467 | 439 | 412 | 388 | 366 | 346 | 328 | 312 | 297 | 283 |  |  | 0.285 | 3 | 3 | 388 | 388 | 366
[11 empty] | 3 | 608 | 580 | 551 | 523 | 496 | 471 | 448 | 426 | 405 | 386 | 369 | 352 | 337 | 323 | 310 | 0.208 | 4 | 4 | 448 | 448 | 426
[11 empty] | 4 | 636 | 612 | 588 | 564 | 540 | 517 | 495 | 474 | 454 | 435 | 417 | 401 | 385 | 370 | 356 | 0.164 | 5 | 5 | 495 | 495 | 474
[11 empty] | 5 | 654 | 635 | 615 | 594 | 574 | 553 | 533 | 513 | 494 | 476 | 459 | 442 | 426 | 411 | 381 | 0.135 | 6 | 6 | 533 | 533 | 513
[11 empty] | 6 | 668 | 652 | 635 | 617 | 599 | 581 | 563 | 545 | 527 | 510 | 494 | 478 | 462 | 422 | 381 | 0.115 | 7 | 7 | 563 | 563 | 545
[11 empty] | 7 | 677 | 664 | 650 | 635 | 619 | 603 | 587 | 570 | 554 | 538 | 523 | 508 | 470 | 422 | 381 | 0.1 | 8 | 8 | 587 | 587 | 570
[11 empty] | 8 | 684 | 673 | 661 | 648 | 634 | 620 | 606 | 591 | 576 | 562 | 547 | 527 | 470 | 422 | 381 | 0.089 | 9 | 9 | 606 | 606 | 591
[11 empty] | 9 | 690 | 680 | 670 | 659 | 647 | 634 | 621 | 608 | 595 | 582 | 568 | 527 | 470 | 422 | 381 | 0.08 | 10 | 10 | 621 | 621 | 608
[11 empty] | 10 | 694 | 686 | 677 | 667 | 667 | 645 | 634 | 622 | 610 | 598 | 586 | 527 | 470 | 422 | 381 | 0.072 | 11 | 11 | 634 | 634 | 622
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.1
[30 empty] | K2 = | 1056
[30 empty] | Db = | 1652
[30 empty] | v = | 587 | plf
1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 581 | 505 | 441 | 390 | 349 | 316 | 288 | 264 | 244 | 266 | 211 | 197 | 185 | 175 | 167 | 0.535 | 1 | 1 | 288 | 288 | 264
[11 empty] | 1 | 1: 757; 2: 665; 3: 592; 4: 532; 5: 482; 6: 437; 7: 399 | 0.317 | 2 | 2 | 399 | 399 | 0
[11 empty] | 2 | 910 | 808 | 725 | 656 | 598 | 549 | 507 | 469 | 434 | 404 | 377 | 354 | 333 |  |  | 0.225 | 3 | 3 | 507 | 507 | 469
[11 empty] | 3 | 1039 | 934 | 845 | 770 | 705 | 650 | 602 | 561 | 527 | 492 | 437 | 387 | 345 | 310 | 279 | 0.174 | 4 | 4 | 602 | 602 | 561
[11 empty] | 4 | 1148 | 1043 | 952 | 873 | 804 | 744 | 692 | 646 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.142 | 5 | 5 | 692 | 692 | 646
[11 empty] | 5 | 1238 | 1137 | 1046 | 966 | 894 | 832 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.12 | 6 | 6 | 776 | 776 | 661
[11 empty] | 6 | 1313 | 1217 | 1128 | 1048 | 976 | 912 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.104 | 7 | 7 | 776 | 776 | 661
[11 empty] | 7 | 1375 | 1285 | 1200 | 1122 | 1050 | 924 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.092 | 8 | 8 | 776 | 776 | 661
[11 empty] | 8 | 1426 | 1343 | 1262 | 1187 | 1116 | 924 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.082 | 9 | 9 | 776 | 776 | 661
[11 empty] | 9 | 1470 | 1392 | 1317 | 1244 | 1118 | 924 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.074 | 10 | 10 | 776 | 776 | 661
[11 empty] | 10 | 1506 | 1435 | 1364 | 1295 | 1118 | 924 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.068 | 11 | 11 | 776 | 776 | 661
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.092
[30 empty] | K2 = | 1056
[30 empty] | Db = | 97
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 776 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 514 | 452 | 402 | 361 | 323 | 292 | 266 | 244 | 225 | 209 | 194 | 182 | 171 | 161 | 153 | 0.642 | 1 | 1 | 266 | 266 | 244
[11 empty] | 1 | 1: 659; 2: 589; 3: 531; 4: 483; 5: 441; 6: 406; 7: 376 | 0.351 | 2 | 2 | 376 | 376 | 0
[11 empty] | 2 | 771 | 701 | 640 | 587 | 542 | 501 | 466 | 436 | 408 | 384 | 361 | 339 | 319 |  |  | 0.242 | 3 | 3 | 466 | 466 | 436
[11 empty] | 3 | 856 | 790 | 730 | 677 | 629 | 586 | 548 | 514 | 484 | 457 | 432 | 387 | 345 | 310 | 279 | 0.184 | 4 | 4 | 548 | 548 | 514
[11 empty] | 4 | 920 | 860 | 804 | 752 | 704 | 661 | 621 | 585 | 553 | 497 | 437 | 387 | 345 | 310 | 279 | 0.149 | 5 | 5 | 621 | 621 | 585
[11 empty] | 5 | 968 | 915 | 863 | 814 | 768 | 725 | 686 | 649 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.125 | 6 | 6 | 686 | 686 | 649
[11 empty] | 6 | 1006 | 959 | 912 | 866 | 822 | 781 | 742 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.108 | 7 | 7 | 742 | 742 | 661
[11 empty] | 7 | 1035 | 993 | 951 | 909 | 868 | 829 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.094 | 8 | 8 | 776 | 776 | 661
[11 empty] | 8 | 1058 | 1021 | 983 | 945 | 907 | 870 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.084 | 9 | 9 | 776 | 776 | 661
[11 empty] | 9 | 1076 | 1043 | 1009 | 974 | 939 | 905 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.076 | 10 | 10 | 776 | 776 | 661
[11 empty] | 10 | 1091 | 1062 | 1031 | 1000 | 967 | 924 | 776 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.069 | 11 | 11 | 776 | 776 | 661
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.094
[30 empty] | K2 = | 1056
[30 empty] | Db = | 567
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 776 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 393 | 346 | 309 | 273 | 244 | 220 | 200 | 183 | 168 | 156 | 145 | 135 | 127 | 120 | 114 | 0.802 | 1 | 1 | 200 | 200 | 183
[11 empty] | 1 | 1: 530; 2: 478; 3: 433; 4: 395; 5: 362; 6: 334; 7: 310 | 0.394 | 2 | 2 | 310 | 310 | 0
[11 empty] | 2 | 626 | 576 | 531 | 491 | 455 | 423 | 395 | 370 | 348 | 328 | 310 | 292 | 275 |  |  | 0.261 | 3 | 3 | 395 | 395 | 370
[11 empty] | 3 | 693 | 648 | 606 | 567 | 531 | 499 | 469 | 442 | 418 | 396 | 376 | 357 | 340 | 310 | 279 | 0.195 | 4 | 4 | 469 | 469 | 442
[11 empty] | 4 | 738 | 700 | 663 | 627 | 593 | 561 | 532 | 504 | 479 | 456 | 434 | 387 | 345 | 310 | 279 | 0.156 | 5 | 5 | 532 | 532 | 504
[11 empty] | 5 | 771 | 739 | 706 | 674 | 642 | 612 | 584 | 557 | 532 | 497 | 437 | 387 | 345 | 310 | 279 | 0.13 | 6 | 6 | 584 | 584 | 557
[11 empty] | 6 | 794 | 767 | 739 | 710 | 682 | 654 | 627 | 602 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.111 | 7 | 7 | 627 | 627 | 602
[11 empty] | 7 | 812 | 788 | 764 | 739 | 713 | 688 | 663 | 639 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.097 | 8 | 8 | 663 | 663 | 639
[11 empty] | 8 | 825 | 805 | 784 | 761 | 739 | 716 | 693 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.086 | 9 | 9 | 693 | 693 | 661
[11 empty] | 9 | 835 | 818 | 799 | 780 | 759 | 739 | 718 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.078 | 10 | 10 | 718 | 718 | 661
[11 empty] | 10 | 843 | 828 | 812 | 794 | 776 | 758 | 739 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.071 | 11 | 11 | 739 | 739 | 661
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.097
[30 empty] | K2 = | 1056
[30 empty] | Db = | 802
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 663 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 329 | 294 | 265 | 241 | 217 | 196 | 178 | 163 | 150 | 138 | 129 | 120 | 112 | 106 | 101 | 1.07 | 1 | 1 | 178 | 178 | 163
[11 empty] | 1 | 1: 427; 2: 395; 3: 365; 4: 338; 5: 314; 6: 293; 7: 274 | 0.45 | 2 | 2 | 274 | 274 | 0
[11 empty] | 2 | 484 | 457 | 431 | 407 | 384 | 362 | 342 | 324 | 307 | 292 | 278 | 365 | 253 |  |  | 0.285 | 3 | 3 | 342 | 342 | 324
[11 empty] | 3 | 517 | 496 | 475 | 454 | 434 | 414 | 395 | 378 | 361 | 345 | 330 | 317 | 304 | 292 | 279 | 0.208 | 4 | 4 | 395 | 395 | 378
[11 empty] | 4 | 538 | 522 | 505 | 487 | 470 | 452 | 435 | 419 | 403 | 388 | 374 | 360 | 345 | 310 | 279 | 0.164 | 5 | 5 | 435 | 435 | 419
[11 empty] | 5 | 551 | 538 | 525 | 510 | 495 | 480 | 466 | 451 | 436 | 422 | 409 | 387 | 345 | 310 | 279 | 0.135 | 6 | 6 | 466 | 466 | 451
[11 empty] | 6 | 560 | 550 | 539 | 527 | 514 | 502 | 489 | 476 | 463 | 450 | 437 | 387 | 345 | 310 | 279 | 0.115 | 7 | 7 | 489 | 489 | 476
[11 empty] | 7 | 567 | 558 | 549 | 539 | 529 | 518 | 506 | 495 | 483 | 472 | 437 | 387 | 345 | 310 | 279 | 0.1 | 8 | 8 | 506 | 506 | 495
[11 empty] | 8 | 572 | 565 | 557 | 548 | 539 | 530 | 520 | 510 | 500 | 489 | 437 | 387 | 345 | 310 | 279 | 0.089 | 9 | 9 | 520 | 520 | 510
[11 empty] | 9 | 575 | 569 | 563 | 555 | 548 | 539 | 531 | 522 | 513 | 497 | 437 | 387 | 345 | 310 | 279 | 0.08 | 10 | 10 | 531 | 531 | 522
[11 empty] | 10 | 578 | 573 | 567 | 561 | 554 | 547 | 540 | 532 | 524 | 497 | 437 | 387 | 345 | 310 | 279 | 0.072 | 11 | 11 | 540 | 540 | 532
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.1
[30 empty] | K2 = | 1056
[30 empty] | Db = | 1652
[30 empty] | v = | 506 | plf
1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 581; 2: 505; 3: 441; 4: 390; 5: 349 | 0.535 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 670; 2: 585; 3: 519; 4: 463; 5: 414; 6: 375; 7: 342 | 0.317 | 2 | 2 | 342 | 342 | 0
[11 empty] | 2 | 754 | 662 | 589 | 530 | 480 | 434 | 397 | 365 | 337 | 313 | 293 | 274 | 258 |  |  | 0.225 | 3 | 3 | 397 | 397 | 365
[11 empty] | 3 | 832 | 735 | 656 | 592 | 538 | 493 | 451 | 415 | 384 | 357 | 333 | 313 | 294 | 279 | 265 | 0.174 | 4 | 4 | 451 | 451 | 415
[11 empty] | 4 | 904 | 803 | 720 | 652 | 594 | 545 | 504 | 465 | 431 | 401 | 374 | 351 | 331 | 310 | 279 | 0.142 | 5 | 5 | 504 | 504 | 465
[11 empty] | 5 | 971 | 867 | 781 | 709 | 648 | 596 | 551 | 512 | 477 | 444 | 415 | 387 | 345 | 310 | 279 | 0.12 | 6 | 6 | 551 | 551 | 512
[11 empty] | 6 | 1032 | 927 | 839 | 764 | 700 | 645 | 597 | 556 | 520 | 488 | 437 | 387 | 345 | 310 | 279 | 0.104 | 7 | 7 | 597 | 597 | 556
[11 empty] | 7 | 1089 | 983 | 893 | 816 | 749 | 692 | 642 | 599 | 560 | 497 | 437 | 387 | 345 | 310 | 279 | 0.092 | 8 | 8 | 642 | 642 | 599
[11 empty] | 8 | 1140 | 1036 | 944 | 866 | 797 | 738 | 686 | 640 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.082 | 9 | 9 | 686 | 686 | 640
[11 empty] | 9 | 1187 | 1084 | 993 | 913 | 843 | 782 | 728 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.074 | 10 | 10 | 728 | 728 | 661
[11 empty] | 10 | 1230 | 1129 | 1038 | 957 | 886 | 824 | 769 | 661 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.068 | 11 | 11 | 769 | 769 | 661
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.092
[30 empty] | K2 = | 1056
[30 empty] | Db = | 97
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 642 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 514; 2: 452; 3: 402; 4: 361; 5: 323 | 0.642 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 589; 2: 523; 3: 468; 4: 423; 5: 386; 6: 351; 7: 320 | 0.351 | 2 | 2 | 320 | 320 | 0
[11 empty] | 2 | 656 | 587 | 529 | 481 | 439 | 404 | 374 | 344 | 318 | 296 | 276 | 259 | 243 |  |  | 0.242 | 3 | 3 | 374 | 374 | 344
[11 empty] | 3 | 715 | 645 | 585 | 534 | 490 | 452 | 420 | 391 | 365 | 339 | 317 | 297 | 280 | 265 | 251 | 0.184 | 4 | 4 | 420 | 420 | 391
[11 empty] | 4 | 767 | 697 | 637 | 584 | 538 | 498 | 463 | 433 | 405 | 381 | 358 | 336 | 316 | 299 | 279 | 0.149 | 5 | 5 | 463 | 463 | 433
[11 empty] | 5 | 812 | 744 | 683 | 630 | 624 | 541 | 505 | 472 | 443 | 418 | 394 | 374 | 345 | 310 | 279 | 0.125 | 6 | 6 | 505 | 505 | 472
[11 empty] | 6 | 852 | 786 | 726 | 672 | 663 | 582 | 544 | 510 | 480 | 453 | 428 | 387 | 345 | 310 | 279 | 0.108 | 7 | 7 | 544 | 544 | 510
[11 empty] | 7 | 886 | 823 | 764 | 711 | 69 | 620 | 581 | 546 | 515 | 486 | 437 | 387 | 345 | 310 | 279 | 0.094 | 8 | 8 | 581 | 581 | 546
[11 empty] | 8 | 916 | 856 | 799 | 747 | 732 | 656 | 616 | 580 | 548 | 497 | 437 | 387 | 345 | 310 | 279 | 0.084 | 9 | 9 | 616 | 616 | 580
[11 empty] | 9 | 942 | 885 | 830 | 779 | 763 | 689 | 649 | 613 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.076 | 10 | 10 | 649 | 649 | 613
[11 empty] | 10 | 965 | 911 | 858 | 809 |  | 720 | 680 | 644 | 570 | 497 | 437 | 387 | 345 | 310 | 279 | 0.069 | 11 | 11 | 680 | 680 | 644
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.094
[30 empty] | K2 = | 1056
[30 empty] | Db = | 567
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 581 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 393; 2: 346; 3: 309; 4: 273; 5: 244 | 0.802 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 466; 2: 415; 3: 373; 4: 338; 5: 308; 6: 279; 7: 254 | 0.394 | 2 | 2 | 254 | 254 | 0
[11 empty] | 2 | 528 | 476 | 431 | 393 | 360 | 332 | 308 | 284 | 262 | 243 | 227 | 212 | 199 |  |  | 0.261 | 3 | 3 | 308 | 308 | 284
[11 empty] | 3 | 580 | 528 | 482 | 433 | 408 | 378 | 352 | 328 | 308 | 287 | 268 | 251 | 236 | 223 | 212 | 0.195 | 4 | 4 | 352 | 352 | 328
[11 empty] | 4 | 623 | 573 | 528 | 488 | 452 | 420 | 392 | 368 | 345 | 326 | 308 | 289 | 272 | 258 | 245 | 0.156 | 5 | 5 | 392 | 392 | 368
[11 empty] | 5 | 659 | 612 | 568 | 528 | 492 | 459 | 430 | 404 | 381 | 360 | 341 | 323 | 308 | 292 | 277 | 0.13 | 6 | 6 | 430 | 430 | 404
[11 empty] | 6 | 689 | 645 | 603 | 563 | 528 | 495 | 466 | 439 | 414 | 392 | 372 | 354 | 337 | 310 | 279 | 0.111 | 7 | 7 | 466 | 466 | 439
[11 empty] | 7 | 715 | 673 | 633 | 595 | 560 | 528 | 498 | 471 | 446 | 423 | 402 | 383 | 345 | 310 | 279 | 0.097 | 8 | 8 | 498 | 498 | 471
[11 empty] | 8 | 736 | 697 | 659 | 623 | 589 | 557 | 528 | 500 | 475 | 452 | 430 | 387 | 345 | 310 | 279 | 0.086 | 9 | 9 | 528 | 528 | 500
[11 empty] | 9 | 753 | 718 | 682 | 648 | 615 | 584 | 555 | 527 | 502 | 479 | 437 | 387 | 345 | 310 | 279 | 0.078 | 10 | 10 | 555 | 555 | 527
[11 empty] | 10 | 768 | 736 | 702 | 670 | 638 | 608 | 580 | 553 | 527 | 497 | 437 | 387 | 345 | 310 | 279 | 0.071 | 11 | 11 | 580 | 580 | 553
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.097
[30 empty] | K2 = | 1056
[30 empty] | Db = | 802
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 498 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 329; 2: 294; 3: 265; 4: 241; 5: 217 | 1.07 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 384; 2: 349; 3: 319; 4: 292; 5: 269; 6: 249; 7: 232 | 0.45 | 2 | 2 | 232 | 232 | 0
[11 empty] | 2 | 426 | 393 | 363 | 336 | 312 | 291 | 272 | 255 | 240 | 226 | 210 | 197 | 185 |  |  | 0.285 | 3 | 3 | 272 | 272 | 255
[11 empty] | 3 | 458 | 428 | 400 | 374 | 350 | 328 | 308 | 290 | 274 | 260 | 246 | 234 | 221 | 209 | 199 | 0.208 | 4 | 4 | 308 | 308 | 290
[11 empty] | 4 | 482 | 455 | 427 | 405 | 381 | 360 | 340 | 322 | 305 | 290 | 276 | 263 | 251 | 240 | 230 | 0.164 | 5 | 5 | 340 | 340 | 322
[11 empty] | 5 | 501 | 477 | 454 | 431 | 408 | 388 | 368 | 350 | 333 | 317 | 303 | 289 | 277 | 265 | 255 | 0.135 | 6 | 6 | 368 | 368 | 350
[11 empty] | 6 | 516 | 495 | 473 | 452 | 431 | 412 | 393 | 375 | 358 | 342 | 328 | 314 | 301 | 289 | 278 | 0.115 | 7 | 7 | 393 | 393 | 375
[11 empty] | 7 | 527 | 509 | 489 | 470 | 451 | 432 | 414 | 397 | 390 | 365 | 350 | 336 | 323 | 310 | 279 | 0.1 | 8 | 8 | 414 | 414 | 397
[11 empty] | 8 | 537 | 520 | 503 | 485 | 467 | 450 | 433 | 416 | 400 | 385 | 371 | 357 | 344 | 310 | 279 | 0.089 | 9 | 9 | 433 | 433 | 416
[11 empty] | 9 | 544 | 529 | 514 | 498 | 481 | 465 | 449 | 433 | 418 | 403 | 389 | 376 | 345 | 310 | 279 | 0.08 | 10 | 10 | 449 | 449 | 433
[11 empty] | 10 | 550 | 537 | 523 | 508 | 493 | 478 | 463 | 448 | 434 | 419 | 406 | 387 | 345 | 310 | 279 | 0.072 | 11 | 11 | 463 | 463 | 448
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.1
[30 empty] | K2 = | 1056
[30 empty] | Db = | 1652
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 414 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 343; 2: 298; 3: 261; 4: 230; 5: 206 | 0.605 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 430; 2: 377; 3: 335; 4: 301; 5: 272; 6: 246; 7: 224 | 0.456 | 2 | 2 | 224 | 224 | 0
[11 empty] | 2 | 508 | 450 | 402 | 363 | 331 | 303 | 279 | 257 | 237 | 221 | 206 | 193 | 182 |  |  | 0.366 | 3 | 3 | 279 | 279 | 257
[11 empty] | 3 | 576 | 515 | 464 | 421 | 385 | 354 | 328 | 305 | 284 | 264 | 247 | 232 | 218 | 207 | 196 | 0.306 | 4 | 4 | 328 | 328 | 305
[11 empty] | 4 | 636 | 573 | 520 | 475 | 436 | 402 | 373 | 348 | 325 | 306 | 288 | 270 | 255 | 241 | 229 | 0.263 | 5 | 5 | 373 | 373 | 348
[11 empty] | 5 | 687 | 625 | 571 | 524 | 483 | 448 | 417 | 389 | 365 | 343 | 324 | 306 | 291 | 276 | 262 | 0.23 | 6 | 6 | 417 | 417 | 389
[11 empty] | 6 | 730 | 671 | 617 | 569 | 527 | 490 | 458 | 428 | 402 | 379 | 358 | 340 | 323 | 307 | 279 | 0.205 | 7 | 7 | 458 | 458 | 428
[11 empty] | 7 | 768 | 710 | 658 | 611 | 568 | 530 | 496 | 466 | 438 | 414 | 392 | 372 | 345 | 310 | 279 | 0.185 | 8 | 8 | 496 | 496 | 466
[11 empty] | 8 | 800 | 745 | 694 | 648 | 605 | 567 | 532 | 501 | 473 | 447 | 424 | 387 | 345 | 310 | 279 | 0.168 | 9 | 9 | 532 | 532 | 501
[11 empty] | 9 | 827 | 776 | 727 | 681 | 639 | 601 | 566 | 534 | 505 | 478 | 437 | 387 | 345 | 310 | 279 | 0.154 | 10 | 10 | 566 | 566 | 534
[11 empty] | 10 | 851 | 803 | 756 | 712 | 671 | 632 | 597 | 565 | 536 | 497 | 437 | 387 | 345 | 310 | 279 | 0.142 | 11 | 11 | 597 | 597 | 565
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.185
[30 empty] | K2 = | 1398
[30 empty] | Db = | 63
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 496 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 304; 2: 267; 3: 238; 4: 213; 5: 191 | 0.726 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 376; 2: 335; 3: 302; 4: 274; 5: 250; 6: 230; 7: 211 | 0.522 | 2 | 2 | 211 | 211 | 0
[11 empty] | 2 | 435 | 393 | 358 | 327 | 301 | 278 | 258 | 241 | 225 | 210 | 197 | 184 | 173 |  |  | 0.48 | 3 | 3 | 258 | 258 | 241
[11 empty] | 3 | 482 | 441 | 406 | 374 | 346 | 322 | 300 | 281 | 264 | 248 | 235 | 222 | 210 | 199 | 189 | 0.334 | 4 | 4 | 300 | 300 | 281
[11 empty] | 4 | 519 | 481 | 446 | 415 | 387 | 361 | 338 | 318 | 299 | 283 | 268 | 254 | 242 | 230 | 220 | 0.283 | 5 | 5 | 338 | 338 | 318
[11 empty] | 5 | 548 | 513 | 481 | 450 | 422 | 396 | 373 | 352 | 333 | 315 | 299 | 284 | 271 | 259 | 247 | 0.246 | 6 | 6 | 373 | 373 | 352
[11 empty] | 6 | 572 | 540 | 509 | 4880 | 453 | 428 | 404 | 383 | 363 | 345 | 328 | 313 | 299 | 286 | 274 | 0.217 | 7 | 7 | 404 | 404 | 383
[11 empty] | 7 | 590 | 562 | 534 | 506 | 480 | 455 | 432 | 411 | 391 | 372 | 355 | 339 | 325 | 310 | 279 | 0.195 | 8 | 8 | 432 | 432 | 411
[11 empty] | 8 | 606 | 580 | 554 | 528 | 504 | 480 | 457 | 436 | 416 | 398 | 380 | 364 | 345 | 310 | 279 | 0.176 | 9 | 9 | 457 | 457 | 436
[11 empty] | 9 | 618 | 595 | 571 | 547 | 524 | 501 | 480 | 459 | 440 | 421 | 404 | 387 | 345 | 310 | 279 | 0.161 | 10 | 10 | 480 | 480 | 459
[11 empty] | 10 | 628 | 607 | 586 | 564 | 542 | 520 | 500 | 480 | 460 | 442 | 425 | 387 | 345 | 310 | 279 | 0.148 | 11 | 11 | 500 | 500 | 480
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.195
[30 empty] | K2 = | 1398
[30 empty] | Db = | 372
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 432 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 232; 2: 205; 3: 182; 4: 161; 5: 144 | 0.907 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 301; 2: 270; 3: 244; 4: 222; 5: 204; 6: 188; 7: 173 | 0.61 | 2 | 2 | 173 | 173 | 0
[11 empty] | 2 | 353 | 323 | 296 | 272 | 251 | 233 | 217 | 203 | 191 | 179 | 167 | 157 | 148 | . |  | 0.459 | 3 | 3 | 217 | 217 | 203
[11 empty] | 3 | 391 | 363 | 337 | 313 | 292 | 273 | 256 | 240 | 227 | 214 | 203 | 192 | 183 | 174 | 165 | 0.368 | 4 | 4 | 256 | 256 | 240
[11 empty] | 4 | 419 | 394 | 370 | 347 | 327 | 307 | 290 | 274 | 259 | 246 | 233 | 222 | 212 | 203 | 194 | 0.307 | 5 | 5 | 290 | 290 | 274
[11 empty] | 5 | 439 | 418 | 396 | 375 | 355 | 337 | 319 | 303 | 288 | 274 | 261 | 250 | 239 | 229 | 219 | 0.264 | 6 | 6 | 319 | 319 | 303
[11 empty] | 6 | 455 | 436 | 417 | 397 | 379 | 361 | 344 | 329 | 314 | 300 | 287 | 275 | 263 | 253 | 243 | 0.231 | 7 | 7 | 344 | 344 | 329
[11 empty] | 7 | 467 | 450 | 433 | 416 | 399 | 382 | 366 | 351 | 336 | 323 | 310 | 297 | 286 | 275 | 265 | 0.206 | 8 | 8 | 366 | 366 | 351
[11 empty] | 8 | 476 | 461 | 446 | 431 | 415 | 400 | 385 | 370 | 356 | 343 | 330 | 318 | 306 | 295 | 279 | 0.185 | 9 | 9 | 385 | 385 | 370
[11 empty] | 9 | 483 | 471 | 457 | 443 | 429 | 415 | 401 | 387 | 373 | 361 | 348 | 336 | 325 | 310 | 279 | 0.168 | 10 | 10 | 401 | 401 | 387
[11 empty] | 10 | 489 | 478 | 466 | 453 | 440 | 427 | 414 | 401 | 389 | 376 | 364 | 353 | 341 | 310 | 279 | 0.154 | 11 | 11 | 414 | 414 | 401
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.206
[30 empty] | K2 = | 1398
[30 empty] | Db = | 526
[11 empty] | 1.5B 20 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 366 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 194; 2: 174; 3: 156; 4: 142; 5: 128 | 1.209 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 245; 2: 225; 3: 207; 4: 191; 5: 177; 6: 165; 7: 154 | 0.733 | 2 | 2 | 154 | 154 | 0
[11 empty] | 2 | 276 | 259 | 243 | 228 | 214 | 201 | 190 | 179 | 169 | 160 | 152 | 145 | 138 |  |  | 0.526 | 3 | 3 | 190 | 190 | 179
[11 empty] | 3 | 297 | 283 | 269 | 255 | 242 | 230 | 219 | 208 | 198 | 189 | 180 | 172 | 165 | 158 | 152 | 0.41 | 4 | 4 | 219 | 219 | 208
[11 empty] | 4 | 310 | 299 | 287 | 275 | 264 | 253 | 242 | 232 | 222 | 213 | 204 | 196 | 188 | 181 | 174 | 0.336 | 5 | 5 | 242 | 242 | 232
[11 empty] | 5 | 319 | 310 | 300 | 290 | 280 | 270 | 260 | 253 | 241 | 233 | 226 | 216 | 208 | 201 | 194 | 0.285 | 6 | 6 | 260 | 260 | 253
[11 empty] | 6 | 325 | 318 | 310 | 301 | 292 | 284 | 275 | 266 | 257 | 249 | 241 | 233 | 226 | 219 | 212 | 0.247 | 7 | 7 | 275 | 275 | 266
[11 empty] | 7 | 330 | 324 | 317 | 310 | 302 | 294 | 286 | 278 | 271 | 263 | 255 | 248 | 241 | 234 | 227 | 0.218 | 8 | 8 | 286 | 286 | 278
[11 empty] | 8 | 334 | 328 | 322 | 316 | 309 | 303 | 296 | 289 | 281 | 274 | 267 | 260 | 254 | 247 | 241 | 0.195 | 9 | 9 | 296 | 296 | 289
[11 empty] | 9 | 336 | 332 | 327 | 321 | 315 | 309 | 303 | 297 | 290 | 284 | 277 | 271 | 265 | 258 | 252 | 0.177 | 10 | 10 | 303 | 303 | 297
[11 empty] | 10 | 338 | 334 | 330 | 325 | 320 | 315 | 309 | 304 | 298 | 292 | 286 | 280 | 274 | 268 | 262 | 0.161 | 11 | 11 | 309 | 309 | 304
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.218
[30 empty] | K2 = | 1398
[30 empty] | Db = | 1084
[30 empty] | v = | 286 | plf
1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[10 empty] | 1 | 0 | 917 | 797 | 701 | 620 | 555 | 502 | 458 | 421 | 389 | 361 | 337 | 315 | 296 | 279 | 264 | 0.615 | 1 | 1 | 458 | 458 | 421
[10 empty] | 2 | 1 | 1: 1148; 2: 1007; 3: 894; 4: 804; 5: 728; 6: 660; 7: 602 | 0.364 | 2 | 2 | 602 | 602 | 0
[10 empty] | 3 | 2 | 1355 | 1199 | 1072 | 968 | 881 | 808 | 746 | 687 | 636 | 592 | 553 | 519 | 489 |  |  | 0.259 | 3 | 3 | 746 | 746 | 687
[10 empty] | 4 | 3 | 1536 | 1372 | 1236 | 1121 | 1025 | 943 | 872 | 811 | 757 | 707 | 661 | 621 | 585 | 553 | 524 | 0.2 | 4 | 4 | 872 | 872 | 811
[10 empty] | 5 | 4 | 1693 | 1527 | 1385 | 1264 | 1160 | 1071 | 993 | 925 | 866 | 813 | 766 | 723 | 681 | 644 | 597 | 0.164 | 5 | 5 | 993 | 993 | 925
[10 empty] | 6 | 5 | 1829 | 1664 | 1520 | 1395 | 1286 | 1191 | 1108 | 1035 | 970 | 912 | 861 | 815 | 737 | 662 | 597 | 0.138 | 6 | 6 | 1108 | 1108 | 1035
[10 empty] | 7 | 6 | 1946 | 1785 | 1642 | 1515 | 1403 | 1304 | 1217 | 1139 | 1070 | 1008 | 933 | 827 | 737 | 662 | 597 | 0.12 | 7 | 7 | 1217 | 1217 | 1139
[10 empty] | 8 | 7 | 2046 | 1892 | 1751 | 1624 | 1511 | 1409 | 1319 | 1238 | 1165 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.106 | 8 | 8 | 1319 | 1319 | 1238
[10 empty] | 9 | 8 | 2131 | 1985 | 1849 | 1724 | 1610 | 1507 | 1415 | 1331 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.094 | 9 | 9 | 1415 | 1415 | 1331
[10 empty] | 10 | 9 | 2205 | 2067 | 1936 | 1814 | 1701 | 1598 | 1505 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.085 | 10 | 10 | 1505 | 1505 | 1413
[10 empty] | 11 | 10 | 2268 | 2138 | 2013 | 1894 | 1784 | 1682 | 1588 | 1413 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.078 | 11 | 11 | 1588 | 1588 | 1413
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.106
[30 empty] | K2 = | 1398
[30 empty] | Db = | 63
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 1319 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 812 | 714 | 635 | 572 | 514 | 464 | 423 | 389 | 359 | 333 | 311 | 291 | 273 | 258 | 243 | 0.739 | 1 | 1 | 423 | 423 | 389
[11 empty] | 1 | 1: 1003; 2: 895; 3: 805; 4: 730; 5: 667; 6: 613; 7: 567 | 0.404 | 2 | 2 | 567 | 567 | 0
[11 empty] | 2 | 1159 | 1049 | 953 | 872 | 801 | 740 | 687 | 641 | 600 | 564 | 527 | 495 | 466 |  |  | 0.278 | 3 | 3 | 687 | 687 | 641
[11 empty] | 3 | 1284 | 1177 | 1081 | 996 | 922 | 856 | 798 | 747 | 702 | 661 | 624 | 573 | 561 | 531 | 503 | 0.212 | 4 | 4 | 798 | 798 | 747
[11 empty] | 4 | 1383 | 1282 | 1189 | 1105 | 1029 | 961 | 900 | 846 | 797 | 752 | 712 | 676 | 643 | 613 | 585 | 0.171 | 5 | 5 | 900 | 900 | 846
[11 empty] | 5 | 1462 | 1369 | 1281 | 1199 | 1124 | 1055 | 993 | 936 | 885 | 838 | 795 | 756 | 721 | 662 | 597 | 0.144 | 6 | 6 | 993 | 993 | 936
[11 empty] | 6 | 1525 | 1440 | 1358 | 1279 | 1206 | 1139 | 1076 | 1018 | 966 | 917 | 873 | 827 | 737 | 662 | 597 | 0.124 | 7 | 7 | 1076 | 1076 | 1018
[11 empty] | 7 | 1575 | 1498 | 1422 | 1349 | 1279 | 1212 | 1151 | 1093 | 1040 | 991 | 933 | 827 | 737 | 662 | 597 | 0.109 | 8 | 8 | 1151 | 1151 | 1093
[11 empty] | 8 | 1616 | 1547 | 1477 | 1408 | 1341 | 1278 | 1218 | 1161 | 1108 | 1058 | 933 | 827 | 737 | 662 | 597 | 0.097 | 9 | 9 | 1218 | 1218 | 1161
[11 empty] | 9 | 1649 | 1587 | 1523 | 1459 | 1396 | 1335 | 1277 | 1222 | 1169 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.087 | 10 | 10 | 1277 | 1277 | 1222
[11 empty] | 10 | 1677 | 1620 | 1562 | 1503 | 1444 | 1386 | 1330 | 1277 | 1219 | 1062 | 933 | 827 | 737 | 662 | 597 | 0.08 | 11 | 11 | 1330 | 1330 | 1277
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.109
[30 empty] | K2 = | 1398
[30 empty] | Db = | 372
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 1151 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 621 | 547 | 487 | 435 | 389 | 351 | 320 | 293 | 270 | 250 | 233 | 218 | 204 | 192 | 181 | 0.923 | 1 | 1 | 320 | 320 | 293
[11 empty] | 1 | 1: 804; 2: 721; 3: 652; 4: 593; 5: 543; 6: 500; 7: 463 | 0.454 | 2 | 2 | 463 | 463 | 0
[11 empty] | 2 | 941 | 860 | 788 | 725 | 669 | 621 | 578 | 541 | 507 | 477 | 449 | 421 | 398 |  |  | 0.301 | 3 | 3 | 578 | 578 | 541
[11 empty] | 3 | 1043 | 967 | 898 | 835 | 778 | 727 | 681 | 640 | 603 | 570 | 539 | 512 | 487 | 464 | 441 | 0.225 | 4 | 4 | 681 | 681 | 640
[11 empty] | 4 | 1117 | 1050 | 986 | 925 | 869 | 818 | 771 | 728 | 889 | 653 | 621 | 591 | 564 | 538 | 515 | 0.18 | 5 | 5 | 771 | 771 | 728
[11 empty] | 5 | 1172 | 1113 | 1055 | 999 | 946 | 896 | 849 | 806 | 766 | 729 | 695 | 664 | 635 | 608 | 583 | 0.15 | 6 | 6 | 849 | 849 | 806
[11 empty] | 6 | 1214 | 1163 | 1111 | 1059 | 1010 | 962 | 917 | 874 | 635 | 797 | 763 | 730 | 700 | 662 | 597 | 0.128 | 7 | 7 | 917 | 917 | 874
[11 empty] | 7 | 1246 | 1201 | 1155 | 1108 | 1062 | 1018 | 975 | 934 | 895 | 858 | 823 | 791 | 737 | 662 | 597 | 0.112 | 8 | 8 | 975 | 975 | 934
[11 empty] | 8 | 1271 | 1232 | 1190 | 1149 | 1107 | 1065 | 1025 | 985 | 948 | 912 | 878 | 827 | 737 | 662 | 597 | 0.099 | 9 | 9 | 1025 | 1025 | 985
[11 empty] | 9 | 1290 | 1258 | 1219 | 1182 | 1143 | 1105 | 1067 | 1030 | 994 | 960 | 926 | 827 | 737 | 662 | 597 | 0.09 | 10 | 10 | 1067 | 1067 | 1030
[11 empty] | 10 | 1306 | 1276 | 1243 | 1209 | 1174 | 1139 | 1104 | 1069 | 1035 | 1002 | 933 | 827 | 737 | 662 | 597 | 0.081 | 11 | 11 | 1104 | 1104 | 1069
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.112
[30 empty] | K2 = | 1398
[30 empty] | Db = | 526
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 975 | plf
SUPPORT FASTENERS: 3/4" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 519 | 464 | 418 | 380 | 347 | 313 | 285 | 281 | 240 | 223 | 207 | 193 | 181 | 170 | 160 | 1.231 | 1 | 1 | 285 | 285 | 281
[11 empty] | 1 | 1: 653; 2: 600; 3: 552; 4: 510; 5: 472; 6: 439; 7: 410 | 0.517 | 2 | 2 | 410 | 410 | 0
[11 empty] | 2 | 738 | 692 | 649 | 608 | 571 | 536 | 505 | 477 | 451 | 427 | 406 | 386 | 368 |  |  | 0.327 | 3 | 3 | 505 | 505 | 477
[11 empty] | 3 | 792 | 754 | 717 | 681 | 646 | 613 | 582 | 554 | 527 | 502 | 479 | 458 | 438 | 420 | 403 | 0.239 | 4 | 4 | 582 | 582 | 554
[11 empty] | 4 | 828 | 797 | 766 | 734 | 703 | 673 | 644 | 617 | 591 | 566 | 543 | 521 | 500 | 481 | 463 | 0.189 | 5 | 5 | 644 | 644 | 617
[11 empty] | 5 | 852 | 827 | 801 | 774 | 747 | 720 | 693 | 668 | 643 | 619 | 597 | 575 | 554 | 535 | 517 | 0.156 | 6 | 6 | 693 | 693 | 668
[11 empty] | 6 | 869 | 849 | 826 | 803 | 780 | 756 | 732 | 709 | 686 | 664 | 642 | 621 | 601 | 682 | 564 | 0.133 | 7 | 7 | 732 | 732 | 709
[11 empty] | 7 | 882 | 864 | 846 | 826 | 806 | 785 | 763 | 742 | 721 | 700 | 680 | 860 | 641 | 623 | 597 | 0.115 | 8 | 8 | 763 | 763 | 742
[11 empty] | 8 | 891 | 877 | 881 | 844 | 828 | 807 | 788 | 789 | 750 | 731 | 712 | 694 | 676 | 658 | 597 | 0.102 | 9 | 9 | 788 | 788 | 789
[11 empty] | 9 | 898 | 886 | 872 | 857 | 842 | 825 | 809 | 792 | 774 | 757 | 739 | 722 | 705 | 662 | 597 | 0.092 | 10 | 10 | 809 | 809 | 792
[11 empty] | 10 | 904 | 893 | 881 | 868 | 855 | 840 | 825 | 810 | 794 | 778 | 762 | 746 | 730 | 662 | 597 | 0.083 | 11 | 11 | 825 | 825 | 810
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.115
[30 empty] | K2 = | 1398
[30 empty] | Db = | 1084
[30 empty] | v = | 763 | plf
1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 754 | 655 | 576 | 510 | 456 | 413 | 377 | 346 | 320 | 297 | 277 | 259 | 244 | 230 | 217 | 0.615 | 1 | 1 | 377 | 377 | 346
[11 empty] | 1 | 1: 982; 2: 863; 3: 768; 4: 691; 5: 627; 6: 570; 7: 521 | 0.364 | 2 | 2 | 521 | 521 | 0
[11 empty] | 2 | 1181 | 1049 | 941 | 851 | 776 | 713 | 658 | 612 | 567 | 528 | 493 | 463 | 436 |  |  | 0.259 | 3 | 3 | 658 | 658 | 612
[11 empty] | 3 | 1349 | 1212 | 1097 | 999 | 916 | 844 | 782 | 728 | 681 | 639 | 601 | 565 | 532 | 484 | 437 | 0.2 | 4 | 4 | 782 | 782 | 728
[11 empty] | 4 | 1490 | 1354 | 1236 | 1133 | 1044 | 966 | 898 | 839 | 786 | 739 | 683 | 605 | 540 | 484 | 437 | 0.164 | 5 | 5 | 898 | 898 | 839
[11 empty] | 5 | 1607 | 1475 | 1358 | 1253 | 1161 | 1079 | 1007 | 943 | 886 | 777 | 683 | 605 | 540 | 484 | 437 | 0.138 | 6 | 6 | 1007 | 1007 | 943
[11 empty] | 6 | 1704 | 1579 | 1465 | 1361 | 1267 | 1183 | 1108 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.12 | 7 | 7 | 1108 | 1108 | 1034
[11 empty] | 7 | 1784 | 1668 | 1558 | 1456 | 1363 | 1278 | 1202 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.106 | 8 | 8 | 1202 | 1202 | 1034
[11 empty] | 8 | 1852 | 1743 | 1639 | 1540 | 1449 | 1365 | 1214 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.094 | 9 | 9 | 1214 | 1214 | 1034
[11 empty] | 9 | 1908 | 1807 | 1709 | 1615 | 1526 | 1443 | 1214 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.085 | 10 | 10 | 1214 | 1214 | 1034
[11 empty] | 10 | 1955 | 1862 | 1770 | 1881 | 1595 | 1445 | 1214 | 1034 | 892 | 777 | 683 | 805 | 540 | 484 | 437 | 0.078 | 11 | 11 | 1214 | 1214 | 1034
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.106
[30 empty] | K2 = | 1398
[30 empty] | Db = | 63
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 1202 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 667 | 587 | 522 | 470 | 422 | 382 | 348 | 320 | 295 | 274 | 256 | 239 | 225 | 212 | 200 | 0.739 | 1 | 1 | 348 | 348 | 320
[11 empty] | 1 | 1: 855; 2: 765; 3: 690; 4: 626; 5: 573; 6: 527; 7: 486 | 0.404 | 2 | 2 | 486 | 486 | 0
[11 empty] | 2 | 1000 | 910 | 831 | 763 | 703 | 651 | 605 | 565 | 530 | 498 | 470 | 443 | 417 |  |  | 0.278 | 3 | 3 | 605 | 605 | 565
[11 empty] | 3 | 1111 | 1025 | 948 | 878 | 816 | 761 | 712 | 666 | 628 | 593 | 561 | 532 | 505 | 482 | 437 | 0.212 | 4 | 4 | 712 | 712 | 666
[11 empty] | 4 | 1194 | 1118 | 1043 | 978 | 914 | 657 | 606 | 760 | 718 | 680 | 845 | 605 | 540 | 484 | 437 | 0.171 | 5 | 5 | 606 | 606 | 760
[11 empty] | 5 | 1257 | 1188 | 1121 | 1057 | 997 | 941 | 890 | 843 | 799 | 759 | 683 | 605 | 540 | 484 | 437 | 0.144 | 6 | 6 | 890 | 890 | 843
[11 empty] | 6 | 1306 | 1244 | 1183 | 1124 | 1087 | 1014 | 983 | 916 | 872 | 777 | 883 | 605 | 540 | 484 | 437 | 0.124 | 7 | 7 | 983 | 983 | 916
[11 empty] | 7 | 1343 | 1289 | 1234 | 1180 | 1127 | 1076 | 1027 | 981 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.109 | 8 | 8 | 1027 | 1027 | 981
[11 empty] | 8 | 1373 | 1325 | 1276 | 1226 | 1177 | 1129 | 1082 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.097 | 9 | 9 | 1082 | 1082 | 1034
[11 empty] | 9 | 1397 | 1354 | 1310 | 1265 | 1219 | 1174 | 1131 | 1034 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.087 | 10 | 10 | 1131 | 1131 | 1034
[11 empty] | 10 | 1416 | 1378 | 1338 | 1297 | 1256 | 1214 | 1172 | 1034 | 892 | 777 | 683 | 805 | 540 | 484 | 437 | 0.08 | 11 | 11 | 1172 | 1172 | 1034
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.109
[30 empty] | K2 = | 1398
[30 empty] | Db = | 372
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 1027 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 511 | 450 | 401 | 358 | 320 | 289 | 283 | 241 | 222 | 206 | 192 | 179 | 168 | 158 | 149 | 0.923 | 1 | 1 | 283 | 283 | 241
[11 empty] | 1 | 1: 668; 2: 620; 3: 562; 4: 512; 5: 470; 6: 434; 7: 402 | 0.454 | 2 | 2 | 402 | 402 | 0
[11 empty] | 2 | 813 | 746 | 689 | 637 | 591 | 550 | 513 | 481 | 452 | 426 | 403 | 382 | 360 | .. |  | 0.301 | 3 | 3 | 513 | 513 | 481
[11 empty] | 3 | 899 | 841 | 787 | 736 | 690 | 648 | 609 | 574 | 543 | 514 | 488 | 464 | 442 | 422 | 403 | 0.225 | 4 | 4 | 609 | 609 | 574
[11 empty] | 4 | 958 | 909 | 860 | 814 | 770 | 729 | 690 | 655 | 622 | 592 | 564 | 538 | 514 | 484 | 437 | 0.18 | 5 | 5 | 690 | 690 | 655
[11 empty] | 5 | 1001 | 959 | 916 | 874 | 834 | 795 | 758 | 723 | 690 | 660 | 631 | 605 | 540 | 484 | 437 | 0.15 | 6 | 6 | 758 | 758 | 723
[11 empty] | 6 | 1031 | 995 | 959 | 922 | 885 | 849 | 814 | 781 | 749 | 719 | 683 | 605 | 540 | 484 | 437 | 0.128 | 7 | 7 | 814 | 814 | 781
[11 empty] | 7 | 1053 | 1023 | 992 | 959 | 926 | 893 | 861 | 830 | 799 | 770 | 683 | 605 | 540 | 484 | 437 | 0.112 | 8 | 8 | 861 | 861 | 830
[11 empty] | 8 | 1071 | 1045 | 1017 | 988 | 959 | 929 | 900 | 871 | 842 | 777 | 683 | 805 | 540 | 484 | 437 | 0.099 | 9 | 9 | 900 | 900 | 871
[11 empty] | 9 | 1084 | 1061 | 1037 | 1012 | 986 | 959 | 932 | 905 | 879 | 777 | 683 | 605 | 540 | 484 | 437 | 0.09 | 10 | 10 | 932 | 932 | 905
[11 empty] | 10 | 1094 | 1075 | 1054 | 1031 | 1008 | 984 | 959 | 934 | 892 | 777 | 683 | 605 | 540 | 484 | 437 | 0.081 | 11 | 11 | 959 | 959 | 934
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.112
[30 empty] | K2 = | 1398
[30 empty] | Db = | 526
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 861 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: Welded | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 427 | 381 | 344 | 312 | 285 | 258 | 234 | 215 | 198 | 183 | 170 | 159 | 149 | 140 | 132 | 1.231 | 1 | 1 | 234 | 234 | 215
[11 empty] | 1 | 1: 555; 2: 512; 3: 473; 4: 439; 5: 408; 6: 380; 7: 355 | 0.517 | 2 | 2 | 355 | 355 | 0
[11 empty] | 2 | 628 | 594 | 560 | 528 | 498 | 470 | 444 | 421 | 399 | 379 | 361 | 344 | 328 |  |  | 0.327 | 3 | 3 | 444 | 444 | 421
[11 empty] | 3 | 671 | 644 | 617 | 590 | 563 | 537 | 513 | 490 | 468 | 448 | 429 | 411 | 394 | 379 | 364 | 0.239 | 4 | 4 | 513 | 513 | 490
[11 empty] | 4 | 698 | 677 | 655 | 632 | 609 | 587 | 565 | 544 | 523 | 504 | 485 | 467 | 450 | 434 | 419 | 0.189 | 5 | 5 | 565 | 565 | 544
[11 empty] | 5 | 716 | 699 | 681 | 662 | 643 | 624 | 604 | 515 | 566 | 548 | 531 | 513 | 497 | 491 | 437 | 0.156 | 6 | 6 | 604 | 604 | 515
[11 empty] | 6 | 727 | 714 | 699 | 684 | 668 | 651 | 634 | 617 | 600 | 584 | 567 | 552 | 536 | 484 | 437 | 0.133 | 7 | 7 | 634 | 634 | 617
[11 empty] | 7 | 736 | 725 | 713 | 700 | 686 | 672 | 657 | 642 | 627 | 612 | 597 | 583 | 540 | 484 | 437 | 0.115 | 8 | 8 | 657 | 657 | 642
[11 empty] | 8 | 742 | 733 | 723 | 712 | 700 | 688 | 675 | 662 | 649 | 635 | 622 | 605 | 540 | 484 | 437 | 0.102 | 9 | 9 | 675 | 675 | 662
[11 empty] | 9 | 746 | 739 | 730 | 721 | 711 | 700 | 669 | 678 | 666 | 654 | 642 | 605 | 540 | 484 | 437 | 0.092 | 10 | 10 | 669 | 669 | 678
[11 empty] | 10 | 750 | 743 | 736 | 728 | 719 | 710 | 700 | 690 | 660 | 689 | 658 | 605 | 540 | 484 | 437 | 0.083 | 11 | 11 | 700 | 700 | 690
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.115
[30 empty] | K2 = | 1398
[30 empty] | Db = | 1084
[30 empty] | v = | 657 | plf
1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 754; 2: 655; 3: 576; 4: 510; 5: 456 | 0.615 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 672; 2: 762; 3: 675; 4: 606; 5: 543; 6: 492; 7: 449 | 0.478 | 2 | 2 | 449 | 449 | 0
[11 empty] | 2 | 983 | 663 | 768 | 691 | 627 | 570 | 521 | 479 | 443 | 412 | 385 | 361 | 340 |  |  | 0.391 | 3 | 3 | 521 | 521 | 479
[11 empty] | 3 | 1066 | 959 | 657 | 773 | 703 | 644 | 593 | 546 | 505 | 470 | 439 | 412 | 368 | 366 | 347 | 0.33 | 4 | 4 | 593 | 593 | 546
[11 empty] | 4 | 1181 | 1049 | 941 | 852 | 777 | 713 | 659 | 612 | 567 | 528 | 493 | 463 | 436 | 412 | 390 | 0.286 | 5 | 5 | 659 | 659 | 612
[11 empty] | 5 | 1269 | 1134 | 1022 | 927 | 648 | 780 | 721 | 671 | 627 | 566 | 548 | 514 | 484 | 458 | 434 | 0.253 | 6 | 6 | 721 | 721 | 671
[11 empty] | 6 | 1349 | 1213 | 1097 | 1000 | 916 | 844 | 782 | 726 | 681 | 639 | 602 | 565 | 532 | 484 | 437 | 0.226 | 7 | 7 | 782 | 782 | 726
[11 empty] | 7 | 1423 | 1288 | 1169 | 1068 | 962 | 907 | 842 | 765 | 734 | 690 | 650 | 605 | 540 | 484 | 437 | 0.204 | 8 | 8 | 842 | 842 | 765
[11 empty] | 8 | 1490 | 1354 | 1236 | 1134 | 1044 | 967 | 899 | 639 | 767 | 740 | 683 | 605 | 540 | 484 | 437 | 0.187 | 9 | 9 | 899 | 899 | 639
[11 empty] | 9 | 1552 | 1418 | 1299 | 1195 | 1104 | 1025 | 954 | 892 | 837 | 777 | 663 | 605 | 540 | 484 | 437 | 0.172 | 10 | 10 | 954 | 954 | 892
[11 empty] | 10 | 1607 | 1476 | 1358 | 1254 | 1162 | 1080 | 1008 | 944 | 687 | 777 | 683 | 605 | 540 | 484 | 437 | 0.159 | 11 | 11 | 1008 | 1008 | 944
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.204
[30 empty] | K2 = | 1398
[30 empty] | Db = | 63
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 842 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 667; 2: 567; 3: 522; 4: 470; 5: 422 | 0.739 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 767; 2: 680; 3: 609; 4: 551; 5: 502; 6: 460; 7: 420 | 0.549 | 2 | 2 | 420 | 420 | 0
[11 empty] | 2 | 855 | 765 | 690 | 627 | 573 | 527 | 488 | 453 | 419 | 390 | 364 | 341 | 321 |  |  | 0.437 | 3 | 3 | 488 | 488 | 453
[11 empty] | 3 | 933 | 842 | 764 | 697 | 640 | 591 | 548 | 511 | 476 | 447 | 418 | 392 | 369 | 349 | 330 | 0.363 | 4 | 4 | 548 | 548 | 511
[11 empty] | 4 | 1001 | 910 | 831 | 763 | 703 | 651 | 606 | 566 | 530 | 499 | 443 | 417 | 394 | 373 | 373 | 0.31 | 5 | 5 | 606 | 606 | 566
[11 empty] | 5 | 1060 | 972 | 893 | 823 | 762 | 708 | 660 | 618 | 580 | 547 | 489 | 465 | 440 | 417 | 417 | 0.271 | 6 | 6 | 660 | 660 | 618
[11 empty] | 6 | 1111 | 1026 | 948 | 879 | 817 | 861 | 761 | 712 | 668 | 628 | 561 | 532 | 506 | 482 | 437 | 0.241 | 7 | 7 | 761 | 761 | 712
[11 empty] | 7 | 1155 | 1074 | 999 | 930 | 867 | 811 | 761 | 715 | 674 | 637 | 604 | 573 | 540 | 484 | 437 | 0.216 | 8 | 8 | 761 | 761 | 715
[11 empty] | 8 | 1194 | 1117 | 1044 | 976 | 914 | 858 | 807 | 760 | 718 | 680 | 645 | 605 | 540 | 484 | 437 | 0.196 | 9 | 9 | 807 | 807 | 760
[11 empty] | 9 | 1228 | 1155 | 1085 | 1019 | 958 | 901 | 850 | 803 | 760 | 721 | 663 | 605 | 540 | 464 | 437 | 0.18 | 10 | 10 | 850 | 850 | 803
[11 empty] | 10 | 1257 | 1168 | 1121 | 1057 | 997 | 942 | 690 | 643 | 800 | 760 | 663 | 605 | 540 | 464 | 437 | 0.166 | 11 | 11 | 690 | 690 | 643
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.216
[30 empty] | K2 = | 1398
[30 empty] | Db = | 372
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 761 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 511; 2: 450; 3: 401; 4: 358; 5: 320 | 0.923 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 607; 2: 541; 3: 466; 4: 440; 5: 402; 6: 367; 7: 335 | 0.645 | 2 | 2 | 335 | 335 | 0
[11 empty] | 2 | 689 | 620 | 562 | 513 | 470 | 434 | 402 | 374 | 346 | 321 | 300 | 261 | 284 |  |  | 0.496 | 3 | 3 | 402 | 402 | 374
[11 empty] | 3 | 757 | 669 | 630 | 578 | 533 | 494 | 460 | 429 | 403 | 379 | 354 | 332 | 312 | 295 | 279 | 0.403 | 4 | 4 | 460 | 460 | 429
[11 empty] | 4 | 813 | 748 | 690 | 637 | 591 | 550 | 514 | 481 | 452 | 426 | 403 | 382 | 360 | 340 | 322 | 0.339 | 5 | 5 | 514 | 514 | 481
[11 empty] | 5 | 860 | 799 | 742 | 690 | 643 | 601 | 563 | 529 | 499 | 471 | 448 | 424 | 403 | 384 | 365 | 0.293 | 6 | 6 | 563 | 563 | 529
[11 empty] | 6 | 899 | 842 | 787 | 737 | 690 | 648 | 609 | 575 | 543 | 514 | 466 | 464 | 442 | 422 | 403 | 0.257 | 7 | 7 | 609 | 609 | 575
[11 empty] | 7 | 932 | 876 | 827 | 776 | 732 | 690 | 652 | 616 | 564 | 554 | 527 | 502 | 479 | 458 | 437 | 0.23 | 8 | 8 | 652 | 652 | 616
[11 empty] | 8 | 959 | 909 | 861 | 814 | 770 | 729 | 691 | 655 | 622 | 592 | 564 | 536 | 514 | 464 | 437 | 0.207 | 9 | 9 | 691 | 691 | 655
[11 empty] | 9 | 961 | 936 | 891 | 846 | 604 | 784 | 726 | 691 | 656 | 627 | 599 | 573 | 540 | 484 | 437 | 0.189 | 10 | 10 | 726 | 726 | 691
[11 empty] | 10 | 1001 | 959 | 917 | 875 | 634 | 795 | 756 | 724 | 691 | 660 | 632 | 605 | 540 | 484 | 437 | 0.174 | 11 | 11 | 756 | 756 | 724
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.23
[30 empty] | K2 = | 1398
[30 empty] | Db = | 526
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 652 | plf
SUPPORT FASTENERS: 5/8" PUDDLE WELD w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 427; 2: 361; 3: 344; 4: 312; 5: 265 | 1.231 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 499; 2: 454; 3: 415; 4: 381; 5: 351; 6: 325; 7: 302 | 0.782 | 2 | 2 | 302 | 302 | 0
[11 empty] | 2 | 555 | 512 | 474 | 439 | 406 | 360 | 355 | 333 | 314 | 296 | 276 | 261 | 245 |  |  | 0.573 | 3 | 3 | 355 | 355 | 333
[11 empty] | 3 | 597 | 556 | 521 | 468 | 457 | 426 | 403 | 360 | 359 | 339 | 322 | 306 | 292 | 277 | 262 | 0.452 | 4 | 4 | 403 | 403 | 360
[11 empty] | 4 | 626 | 594 | 560 | 528 | 498 | 470 | 445 | 421 | 399 | 379 | 351 | 344 | 329 | 314 | 301 | 0.373 | 5 | 5 | 445 | 445 | 421
[11 empty] | 5 | 653 | 622 | 592 | 562 | 533 | 507 | 461 | 458 | 436 | 415 | 397 | 379 | 363 | 346 | 334 | 0.318 | 6 | 6 | 461 | 461 | 458
[11 empty] | 6 | 672 | 645 | 617 | 590 | 563 | 536 | 513 | 490 | 469 | 448 | 429 | 411 | 394 | 379 | 364 | 0.277 | 7 | 7 | 513 | 513 | 490
[11 empty] | 7 | 666 | 663 | 636 | 613 | 588 | 564 | 541 | 519 | 498 | 478 | 459 | 441 | 424 | 408 | 393 | 0.245 | 8 | 8 | 541 | 541 | 519
[11 empty] | 8 | 698 | 677 | 655 | 632 | 610 | 587 | 565 | 544 | 523 | 504 | 465 | 467 | 450 | 434 | 419 | 0.22 | 9 | 9 | 565 | 565 | 544
[11 empty] | 9 | 708 | 669 | 669 | 649 | 626 | 607 | 566 | 566 | 546 | 527 | 509 | 492 | 475 | 459 | 437 | 0.199 | 10 | 10 | 566 | 566 | 566
[11 empty] | 10 | 716 | 699 | 681 | 662 | 643 | 624 | 604 | 565 | 567 | 548 | 531 | 514 | 497 | 462 | 437 | 0.182 | 11 | 11 | 604 | 604 | 565
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.245
[30 empty] | K2 = | 1398
[30 empty] | Db = | 1084
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 541 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/7 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 454; 2: 395; 3: 347; 4: 307; 5: 275 | 0.696 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 570; 2: 500; 3: 444; 4: 399; 5: 362; 6: 327; 7: 299 | 0.525 | 2 | 2 | 299 | 299 | 0
[11 empty] | 2 | 673 | 596 | 533 | 481 | 438 | 402 | 371 | 342 | 316 | 294 | 275 | 258 | 243 |  |  | 0.422 | 3 | 3 | 371 | 371 | 342
[11 empty] | 3 | 163 | 682 | 614 | 558 | 510 | 469 | 434 | 403 | 377 | 352 | 329 | 309 | 291 | 275 | 261 | 0.352 | 4 | 4 | 434 | 434 | 403
[11 empty] | 4 | 842 | 759 | 689 | 629 | 577 | 533 | 494 | 461 | 431 | 405 | 381 | 360 | 339 | 321 | 304 | 0.303 | 5 | 5 | 494 | 494 | 461
[11 empty] | 5 | 909 | 828 | 756 | 694 | 640 | 593 | 552 | 515 | 483 | 454 | 429 | 406 | 385 | 366 | 347 | 0.265 | 6 | 6 | 552 | 552 | 515
[11 empty] | 6 | 967 | 888 | 817 | 754 | 698 | 649 | 606 | 567 | 533 | 502 | 475 | 450 | 427 | 407 | 388 | 0.236 | 7 | 7 | 606 | 606 | 567
[11 empty] | 7 | 1016 | 941 | 871 | 808 | 752 | 102 | 657 | 611 | 580 | 548 | 519 | 492 | 468 | 446 | 426 | 0.212 | 8 | 8 | 657 | 657 | 611
[11 empty] | 8 | 1059 | 987 | 919 | 858 | 801 | 751 | 705 | 663 | 626 | 592 | 561 | 533 | 507 | 484 | 437 | 0.193 | 9 | 9 | 705 | 705 | 663
[11 empty] | 9 | 1095 | 1027 | 963 | 902 | 847 | 796 | 749 | 707 | 669 | 634 | 602 | 572 | 540 | 484 | 437 | 0.177 | 10 | 10 | 749 | 749 | 707
[11 empty] | 10 | 1126 | 1063 | 1001 | 942 | 888 | 837 | 791 | 748 | 709 | 673 | 640 | 805 | 540 | 484 | 437 | 0.164 | 11 | 11 | 791 | 791 | 748
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.212
[30 empty] | K2 = | 1398
[30 empty] | Db = | 63
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 657 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/5 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 402; 2: 353; 3: 315; 4: 283; 5: 254 | 0.835 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 498; 2: 444; 3: 399; 4: 362; 5: 331; 6: 304; 7: 281 | 0.601 | 2 | 2 | 281 | 281 | 0
[11 empty] | 2 | 576 | 521 | 474 | 433 | 398 | 368 | 341 | 318 | 298 | 280 | 262 | 246 | 232 |  |  | 0.469 | 3 | 3 | 341 | 341 | 318
[11 empty] | 3 | 638 | 585 | 537 | 495 | 458 | 426 | 397 | 372 | 349 | 329 | 311 | 294 | 279 | 264 | 250 | 0.385 | 4 | 4 | 397 | 397 | 372
[11 empty] | 4 | 687 | 637 | 591 | 549 | 512 | 478 | 448 | 421 | 396 | 374 | 355 | 337 | 320 | 305 | 291 | 0.326 | 5 | 5 | 448 | 448 | 421
[11 empty] | 5 | 726 | 680 | 636 | 596 | 559 | 525 | 494 | 466 | 440 | 417 | 396 | 377 | 359 | 343 | 328 | 0.283 | 6 | 6 | 494 | 494 | 466
[11 empty] | 6 | 757 | 715 | 675 | 636 | 600 | 566 | 535 | 501 | 481 | 457 | 435 | 414 | 396 | 376 | 362 | 0.25 | 7 | 7 | 535 | 535 | 501
[11 empty] | 7 | 782 | 744 | 706 | 670 | 636 | 603 | 573 | 544 | 518 | 493 | 470 | 449 | 430 | 412 | 395 | 0.224 | 8 | 8 | 573 | 573 | 544
[11 empty] | 8 | 802 | 768 | 733 | 700 | 667 | 635 | 606 | 578 | 561 | 527 | 504 | 482 | 462 | 444 | 426 | 0.203 | 9 | 9 | 606 | 606 | 578
[11 empty] | 9 | 818 | 788 | 756 | 725 | 694 | 664 | 635 | 608 | 562 | 557 | 535 | 513 | 493 | 474 | 437 | 0.185 | 10 | 10 | 635 | 635 | 608
[11 empty] | 10 | 832 | 604 | 775 | 746 | 717 | 689 | 661 | 635 | 610 | 586 | 563 | 541 | 521 | 484 | 437 | 0.17 | 11 | 11 | 661 | 661 | 635
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.224
[30 empty] | K2 = | 1398
[30 empty] | Db = | 372
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 573 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/4 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 308; 2: 271; 3: 241; 4: 215; 5: 193 | 1.044 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 399; 2: 358; 3: 324; 4: 294; 5: 270; 6: 248; 7: 230 | 0.702 | 2 | 2 | 230 | 230 | 0
[11 empty] | 2 | 467 | 427 | 391 | 360 | 333 | 309 | 288 | 269 | 252 | 237 | 224 | 210 | 197 |  |  | 0.528 | 3 | 3 | 288 | 288 | 269
[11 empty] | 3 | 518 | 480 | 446 | 415 | 387 | 382 | 339 | 318 | 300 | 283 | 288 | 255 | 242 | 231 | 220 | 0.424 | 4 | 4 | 339 | 339 | 318
[11 empty] | 4 | 555 | 521 | 490 | 460 | 432 | 407 | 384 | 382 | 343 | 325 | 309 | 294 | 281 | 288 | 257 | 0.354 | 5 | 5 | 384 | 384 | 382
[11 empty] | 5 | 582 | 553 | 524 | 497 | 470 | 448 | 423 | 401 | 381 | 363 | 346 | 331 | 316 | 303 | 290 | 0.304 | 6 | 6 | 423 | 423 | 401
[11 empty] | 6 | 602 | 577 | 552 | 526 | 502 | 478 | 456 | 435 | 415 | 397 | 380 | 364 | 349 | 335 | 322 | 0.266 | 7 | 7 | 456 | 456 | 435
[11 empty] | 7 | 618 | 596 | 573 | 550 | 528 | 506 | 485 | 465 | 446 | 427 | 410 | 394 | 378 | 364 | 351 | 0.237 | 8 | 8 | 485 | 485 | 465
[11 empty] | 8 | 630 | 611 | 591 | 570 | 550 | 529 | 509 | 490 | 471 | 454 | 437 | 421 | 405 | 391 | 377 | 0.213 | 9 | 9 | 509 | 509 | 490
[11 empty] | 9 | 640 | 623 | 605 | 587 | 568 | 549 | 530 | 512 | 494 | 477 | 481 | 445 | 430 | 416 | 402 | 0.194 | 10 | 10 | 530 | 530 | 512
[11 empty] | 10 | 648 | 633 | 617 | 600 | 563 | 566 | 548 | 531 | 515 | 498 | 482 | 467 | 452 | 438 | 424 | 0.178 | 11 | 11 | 548 | 548 | 531
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.237
[30 empty] | K2 = | 1398
[30 empty] | Db = | 526
[11 empty] | 1.5B 18 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF) | [18 empty] | v = | 485 | plf
SUPPORT FASTENERS: #12 TEK SCREWS w/ 36/3 PATTERN
[11 empty] | SIDELAP FASTENERS: #10 TEK SCREWS | [17 empty] | Interpolate for Deck Shear Capacity, v
[11 empty] | # of Sidelap Fasteners | 1: DIAPHRAGM SHEAR STRENGTH (PLF) | K1 |  |  | Span(table) | Span | Span(table)
[12 empty] | 1: DECK SPAN (FT-IN) |  |  |  | 7 | Span Index: | 8
[12 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 |  | t Index: | t Index: | 6 | 6 | 6.5
[11 empty] | 0 | 1: 257; 2: 230; 3: 207; 4: 188; 5: 172 | 1.392 | 1 | 1 | 0 | 0 | 0
[11 empty] | 1 | 1: 324; 2: 298; 3: 274; 4: 253; 5: 234; 6: 218; 7: 204 | 0.843 | 2 | 2 | 204 | 204 | 0
[11 empty] | 2 | 366 | 344 | 322 | 302 | 283 | 267 | 251 | 237 | 224 | 212 | 202 | 192 | 183 |  |  | 0.605 | 3 | 3 | 251 | 251 | 237
[11 empty] | 3 | 393 | 374 | 356 | 338 | 321 | 305 | 290 | 275 | 262 | 250 | 238 | 228 | 218 | 209 | 201 | 0.472 | 4 | 4 | 290 | 290 | 275
[11 empty] | 4 | 410 | 395 | 380 | 365 | 349 | 334 | 320 | 307 | 294 | 281 | 270 | 259 | 249 | 240 | 231 | 0.387 | 5 | 5 | 320 | 320 | 307
[11 empty] | 5 | 422 | 410 | 397 | 384 | 371 | 357 | 344 | 332 | 320 | 308 | 297 | 286 | 276 | 266 | 257 | 0.327 | 6 | 6 | 344 | 344 | 332
[11 empty] | 6 | 431 | 421 | 410 | 399 | 387 | 375 | 364 | 352 | 341 | 330 | 319 | 309 | 299 | 290 | 280 | 0.284 | 7 | 7 | 364 | 364 | 352
[11 empty] | 7 | 437 | 429 | 419 | 410 | 400 | 389 | 379 | 369 | 358 | 348 | 336 | 328 | 319 | 310 | 301 | 0.251 | 8 | 8 | 379 | 379 | 369
[11 empty] | 8 | 442 | 434 | 427 | 418 | 410 | 401 | 391 | 382 | 373 | 363 | 354 | 345 | 336 | 327 | 319 | 0.224 | 9 | 9 | 391 | 391 | 382
[11 empty] | 9 | 445 | 439 | 432 | 425 | 418 | 410 | 401 | 393 | 384 | 376 | 367 | 359 | 350 | 342 | 334 | 0.203 | 10 | 10 | 401 | 401 | 393
[11 empty] | 10 | 448 | 443 | 437 | 431 | 424 | 417 | 409 | 402 | 394 | 386 | 379 | 371 | 363 | 355 | 348 | 0.186 | 11 | 11 | 409 | 409 | 402
[11 empty] | Span Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  |  | K1 = | 0.251
[30 empty] | K2 = | 1398
[30 empty] | Db = | 1084
[30 empty] | v = | 379 | plf
B
L
deck

## AXIALDECK
AXIAL DECK | [16 empty] | Version 1.0 | Version 1.0
AXIAL CAPACITY OF 1 1/2" TYPE 'B' (WIDE RIB) ROOF DECK | [8 empty] | CALCULATIONS:
Using Vulcraft Steel Roof Deck (ICC ER-3415)
Job Name: |  |  |  | Subject: |  | Date: | 2026-07-30 06:25
Job Number: |  |  |  | Originator: |  | Checker: |  | 1.5B22 |  | VULCRAFT SECTION PROPERTIES
1.5B20
Input Data: |  |  |  |  | Member Properties: |  |  | 1.5B18 |  | GAGE | thk, in | Wt, psf | In, in4/ft | +S, in3/ft | -S, in3/ft | Fy (ksi)
Deck: |  |  |  |  | Gage= | 22 | in. | 3/4"Φ Puddle Weld |  | 22 | 0.0295 | 1.78 | 0.183 | 0.186 | 0.192 | 33
| Deck Size: | 1.5B22 |  |  | Thickness,t = | 0.0295 | in. | 5/8"Φ Puddle Weld |  | 20 | 0.0358 | 2.14 | 0.222 | 0.234 | 0.247 | 33
| Deck Length, L = | 6.9 | ft. |  | Wt (psf) = | 1.78 | psf | #12 TEK Screws |  | 18 | 0.0474 | 2.82 | 0.295 | 0.318 | 0.327 | 33
| Dead Load, DL = | 20 | psf |  | In = | 0.183 | in.^4 | Welded
| Live Load, LL = | 20 | psf |  | +S (in4) | 0.186 | in.^3 | #10 TEK Screws | [10 empty] | 1.5B22 ALLOWABLE DIAPHRAGM SHEAR STRENGTH (PLF)
| Unfactored Wall Load, Fp = | 750 | plf |  | -S (in4) | 0.192 | in.^3 | 0 | [10 empty] | SUPPORT FASTENERS: Fn = w/ 0.75 PATTERN
[5 empty] | Fy | 33 | ksi | 1 | [10 empty] | SIDELAP FASTENERS:
[8 empty] | 2 | [10 empty] | # of Sidelap Fasteners | DIAPHRAGM SHEAR STRENGTH (PLF)
[8 empty] | 3 | [11 empty] | DECK SPAN (FT-IN)
[8 empty] | 4 | [11 empty] | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10
[8 empty] | 5 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Analysis: | [7 empty] | 6 | [10 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Properties: | [7 empty] | 7 | [10 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter Length, Lp = | 17.53 | in./ ft. |  |  |  |  | 8 | [10 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Area, A = | 0.51714 | in2 | A = L x t |  |  |  | 9 | [10 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| r = | 0.59487 | in. | r = (In / A) ^ 0.5 |  |  |  | 10 | [10 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| K = | 1 |  |  | (AISI C4.1-1) |  |  | 36/7 | [10 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fe = | 14.7735 | ksi | Fe = π2E / (KL / r)2 |  |  |  | 36/5 | [10 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E = | 29000 | ksi |  |  |  |  | 36/4 | [10 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| λc = | 1.4946 |  | λc = (Fy / Fe) ^ 0.5 |  |  |  | 36/3 | [10 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fn = | 48.5031 |  | Fn = 0.658λc^2 Fy (for λc < 1.5) | [14 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deck Capacity (AISI C.5.2.1)
| M = | 0.23805 | ft kip | M = (DL + LL) L^2 / 8
| P = | 0.75 | kip / ft | P = Fp
| Pe = | 7.6399 | kip / ft | Pe = π2 E In / (KL / r)2
| Mn = | 2.7479 | ft kip / ft | Mn = (+)S Fe
| Pn = | 25.0827 | kip / ft | Pn = A Fn
Axial Stress
| Ratio, ASR = | 0.040367 | < 0.15 | ACSR = 0.75 Ωc P / Pn |  |  | OK
(0.75 from AISI A.4.1.2)
| Ωc = | 1.8
Combined Stress
| Ratio, CSR = | 0.19327 | < 1.0 | CSR = 0.75 Ωc P / Pn + Ωb M Cm / (α Mn) |  |  | OK
| Ωb = | 1.67
| Cm = | 1
| α = | 0.94618 |  | α = 1 - Ωc P / Pn
Comments:
Note on C13: 12.11.2 Anchorage of Concrete or Masonry Structural Walls. The anchorage of concrete or masonry structural walls to supporting construction shall provide a direct connection capable of resisting the greater of the following: a. The force set forth in Section 12.11.1 b. A force of 400SDS I lb/ linear ft (5.84SDS I kN/m) of wall c. 280 lb/linear ft (4.09 kN/m) of wall 12.11.2.1 Anchorage of Concrete or Masonry Structural Walls to Flexible Diaphragms. In addition to the requirements set forth in Section 12.11.2, anchorage of concrete or masonry structural walls to flexible diaphragms in structures assigned to Seismic Design Category C, D, E, or F shall have the strength to develop the out-of-plane force given by Eq. 12.11-1 Fp = 0.8 SDS I Wp (12.11.1) (ASCE 7-05)
L
Fp